## BSM2 OL (1 year)
Ring test BSM 1G |  | Openloop
Model component tested: | COMPLETE BSM1G | STATUS: | Integrated system | Dynamic | Openloop
See detailed specifications at the end of this sheet!
Test of BSM1G for full dynamics in openloop based on the finalised BSM2 and finalised evaluation criteria
Simulation procedure: simulate to steady state using CONSTANT INFLUENT and use final state variable values for initial values for dynamic simulation.
Run full 14 days simulation using input file from BSM web site and base evaluation on the last 7 days, i.e. from beginning of day 7.
Evaluation is based on data every 15 minutes and uses zero-order hold (forward Euler) for integration between measurements.
PLANT EVALUATION 1 YEAR (364 DAYS)
Effluent average concentrations based on load, including bypass
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Effluent average flow rate |  | m3/d |  |  | 18061.1695 |  | 18061.1677 |  | 18061.1686 | 0.0012728 | 0.0018
Effluent average SI concentration |  | g COD/m3 |  |  | 30 |  | 30 |  | 30 | 0 | 0
Effluent average SS concentration |  | g COD/m3 |  |  | 1.2119 |  | 1.2215 |  | 1.2167 | 0.0067882 | 0.0096
Effluent average XI concentration |  | g COD/m3 |  |  | 4.7007 |  | 4.6962 |  | 4.6985 | 0.003182 | 0.0045
Effluent average XS concentration |  | g COD/m3 |  |  | 0.21508 |  | 0.22139 |  | 0.21824 | 0.0044618 | 0.00631
Effluent average XBH concentration |  | g COD/m3 |  |  | 9.8119 |  | 9.8352 |  | 9.8236 | 0.016476 | 0.0233
Effluent average XBA1 concentration |  | g COD/m3 |  |  | 0.52312 |  | 0.51585 |  | 0.51948 | 0.0051407 | 0.00727
Effluent average XP concentration |  | g COD/m3 |  |  | 1.7231 |  | 1.6912 |  | 1.7071 | 0.022557 | 0.0319
Effluent average SO concentration |  | g -COD/m3 |  |  | 3.5801 |  | 3.5476 |  | 3.5638 | 0.022981 | 0.0325
Effluent average SNO3 concentration |  | g N/m3 |  |  | 14.7235 |  | 14.9205 |  | 14.822 | 0.1393 | 0.197 | 0.026475
Effluent average SNH concentration (limit = 4 g N/m3) |  | g N/m3 |  |  | 1.6374 |  | 1.7265 |  | 1.682 | 0.063003 | 0.0891 | 0.20534
Effluent average SND concentration |  | g N/m3 |  |  | 0.55553 |  | 0.55713 |  | 0.55633 | 0.0011314 | 0.0016
Effluent average XND concentration |  | g N/m3 |  |  | 0.015963 |  | 0.016357 |  | 0.01616 | 0.0002786 | 0.000394
Effluent average SALK concentration |  | mol HCO3-/m3 |  |  | 3.806 |  | 3.7995 |  | 3.8028 | 0.0045962 | 0.0065
Effluent average TSS concentration (limit = 30 g SS/m3) |  | g/m3 |  |  | 12.8571 |  | 12.8541 |  | 12.8556 | 0.0021213 | 0.003
Effluent average Temperature |  | deg C |  |  | 15 |  | 15 |  | 15 | 0 | 0
Effluent average SNO2 conc |  | g N/m3 |  |  | 0.043797 |  | 0.026941 |  | 0.035369 | 0.011919 | 0.016856
Effluent average SNO conc |  | g N/m3 |  |  | 0.0026856 |  | 0.0018406 |  | 0.0022631 | 0.00059751 | 0.000845
Effluent average SN2O conc |  | g N/m3 |  |  | 0.001433 |  | 0.00097381 |  | 0.0012034 | 0.0003247 | 0.00045919
Effluent average SN2 conc |  | g N/m3 |  |  | 13.3924 |  | 13.3896 |  | 13.391 | 0.0019799 | 0.0028
Effluent average XBA2 conc |  | g COD/m3 |  |  | 0.16899 |  | 0.17907 |  | 0.17403 | 0.0071276 | 0.01008
Effluent average Kjeldahl N conc |  | g N/m3 |  |  | 3.4977 |  | 3.5888 |  | 3.5433 | 0.064417
Effluent average total N concentration (limit = 18 g N/l) |  | g N/m3 |  |  | 18.2691 |  | 18.539 |  | 18.4041 | 0.19085 | 0.2699
Effluent average total COD concentration (limit = 100 g COD/m3) |  | g COD/m3 |  |  | 48.3548 |  | 48.3603 |  | 48.3576 | 0.0038891 | 0.0055
Effluent average BOD5 concentration (limit = 10 g/m3) |  | g/m3 |  |  | 3.169 |  | 3.1716 |  | 3.1703 | 0.0018385 | 0.0026
Effluent average load, including bypass
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Effluent average SI load |  | kg COD/day |  |  | 541.835 |  | 541.839 |  | 541.837 | 0.0028059 | 0.0039682
Effluent average SS load |  | kg COD/day |  |  | 22.0611 |  | 22.1712 |  | 22.1161 | 0.077848 | 0.11009
Effluent average XI load |  | kg COD/day |  |  | 84.8182 |  | 84.607 |  | 84.7126 | 0.14932 | 0.21118
Effluent average XS load |  | kg COD/day |  |  | 3.9985 |  | 3.9979 |  | 3.9982 | 0.00040583 | 0.00057393
Effluent average XBH load |  | kg COD/day |  |  | 177.6347 |  | 177.3802 |  | 177.5075 | 0.17993 | 0.25446
Effluent average XBA1 load |  | kg COD/day |  |  | 9.3169 |  | 9.2664 |  | 9.2916 | 0.035713 | 0.050506
Effluent average XP load |  | kg COD/day |  |  | 30.5443 |  | 30.5167 |  | 30.5305 | 0.01953 | 0.027619
Effluent average SO load |  | kg -COD/day |  |  | 64.0746 |  | 63.7135 |  | 63.8941 | 0.25533 | 0.36109
Effluent average SNO3 load |  | kg N/day |  |  | 269.4812 |  | 265.318 |  | 267.3996 | 2.9438 | 4.1632
Effluent average SNH load |  | kg N/day |  |  | 31.1827 |  | 34.7911 |  | 32.9869 | 2.5516 | 3.6084
Effluent average SND load |  | kg N/day |  |  | 10.0624 |  | 10.0991 |  | 10.0808 | 0.025984 | 0.036747
Effluent average XND load |  | kg N/day |  |  | 0.29543 |  | 0.29537 |  | 0.2954 | 4.5702e-05 | 6.4632e-05
Effluent average SALK load |  | kmol HCO3-/day |  |  | 68.6241 |  | 69.2192 |  | 68.9216 | 0.42079 | 0.59508
Effluent average TSS load |  | kg/day |  |  | 232.16 |  | 231.7343 |  | 231.9471 | 0.30104 | 0.42574
Effluent average SNO2 load |  | kg N/day |  |  | 0.48658 |  | 0.59122 |  | 0.5389 | 0.073989 | 0.10464
Effluent average SNO load |  | kg N/day |  |  | 0.033244 |  | 0.038883 |  | 0.036063 | 0.0039871 | 0.0056387
Effluent average SN2O load |  | kg N/day |  |  | 0.017588 |  | 0.020631 |  | 0.01911 | 0.0021518 | 0.0030431
Effluent average SN2 load |  | kg N/day |  |  | 241.8326 |  | 241.1925 |  | 241.5125 | 0.45264 | 0.64013
Effluent average XBA2 load |  | kg COD/day |  |  | 3.2341 |  | 3.2108 |  | 3.2224 | 0.016509 | 0.023347
Effluent average Kjeldahl N load |  | kg N/day |  |  | 64.8182 |  | 67.2817 |  | 66.0499 | 1.7419 | 2.4635
Effluent average total N load |  | kg N/day |  |  | 334.8368 |  | 332.5997 |  | 333.7182 | 1.5819 | 2.2371
Effluent average total COD load |  | kg COD/day |  |  | 873.4428 |  | 872.9892 |  | 873.216 | 0.32076 | 0.45362
Effluent average BOD5 load |  | kg/day |  |  | 50.2576 |  | 50.2095 |  | 50.2335 | 0.034027 | 0.048121
Other output quality variables
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Influent quality (I.Q.) index |  | kg poll.units/day |  |  | 52174.9256 |  | 52081.1978 |  | 52128.0617 | 66.2756 | 93.7278
Effluent quality (E.Q.) index |  | kg poll.units/day |  |  | 6088.7156 |  | 6108.7714 |  | 6098.7435 | 14.1816 | 20.0558
Average sludge production for disposal per day |  | kg SS/day |  |  | 2371.9556 |  | 2371.0818 |  | 2371.5187 | 0.61784 | 0.87376
Average sludge production released into effluent per day |  | kg SS/day |  |  | 232.16 |  | 231.7477 |  | 231.9538 | 0.29155 | 0.41232
Total average sludge production per day |  | kg SS/day |  |  | 2604.1156 |  | 2602.8295 |  | 2603.4726 | 0.90939 | 1.2861
'Energy' related variables
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Average aeration energy |  | kWh/d |  |  | 4283.3778 |  | 7710.08 |  | 5996.7289 | 2423.0444 | 3426.7022
Average pumping energy |  | kWh/d |  |  | 388.17 |  | 503.67 |  | 445.92 | 81.6708 | 115.5
Average carbon source dosage |  | kg COD/day |  |  | 0 |  | 0 |  | 0 | 0 | 0
Average mixing energy |  | kWh/d |  |  | 240 |  | 240.3571 |  | 240.1786 | 0.25254 | 0.35714
Operational cost index
Variable (including weight factor) |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Sludge production cost index |  | – |  |  | 7115.8669 |  | 13014.1476 |  | 10065.0073 | 4170.7143 | 5898.2807
Aeration energy cost index |  | – |  |  | 4283.3778 |  | 7710.08 |  | 5996.7289 | 2423.0444 | 3426.7022
Pumping energy cost index |  | – |  |  | 388.17 |  | 503.67 |  | 445.92 | 81.6708 | 115.5
Carbon source dosage cost index |  | – |  |  | 0 |  | 0 |  | 0 | 0 | 0
Mixing energy cost index |  | – |  |  | 240 |  | 240.3571 |  | 240.1786 | 0.25254 | 0.35714
Total Operational Cost Index (OCI) |  | – |  |  | 12027.4147 |  | 21468.2548 |  | 16747.8347 | 6675.682 | 9440.8401
Effluent violations
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
95% percentile of effluent SNH (Ammonia95) |  | g N/m3 |  |  |  |  | 6.7921 |  | 6.7921 | #DIV/0! | 0
95% percentile of effluent total N (TN95) |  | g N/m3 |  |  |  |  | 22.5423 |  | 22.5423 | #DIV/0! | 0
95% percentile of effluent TSS (TSS95) |  | g COD/m3 |  |  |  |  | 15.5488 |  | 15.5488 | #DIV/0! | 0
Maximum effluent total N limit (18 mg N/l) was violated | [6 empty] | 0
during: |  | days |  |  |  |  | 1.7917 |  | 1.7917 | #DIV/0! | 0
% of total evaluation time: |  | % |  |  |  |  | 25.5952 |  | 25.5952 | #DIV/0! | 0
number of violations: |  | – |  |  |  |  | 7 |  | 7 | #DIV/0! | 0
Maximum effluent total COD limit (100 mg COD/l) was violated | [6 empty] | 0
during: |  | days |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
% of total evaluation time: |  | % |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
number of violations: |  | – |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
Maximum effluent ammonia limit (4 mg N/l) was violated | [6 empty] | 0
during: |  | days |  |  | 0.76042 |  | 0.8125 |  | 0.78646 | 0.036826 | 0.05208
% of total evaluation time: |  | % |  |  | 10.8631 |  | 11.6071 |  | 11.2351 | 0.52612 | 0.74404
number of violations: |  | – |  |  | 5 |  | 5 |  | 5 | 0 | 0
Maximum effluent TSS limit (30 mg SS/l) was violated | [6 empty] | 0
during: |  | days |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
% of total evaluation time: |  | % |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
number of violations: |  | – |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
Maximum effluent BOD5 limit (10 mg/l) was violated | [6 empty] | 0
during: |  | days |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
% of total evaluation time: |  | % |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
number of violations: |  | – |  |  |  |  | 0 |  | 0 | #DIV/0! | 0
N2O Emissions
-------------------
N2O emission during nitrification/denitrification (ANOX1) |  | kg N2O/d |  |  | 0.01053 |  | 0.016408 |  | 0.013469 | 0.0041562 | 0.0058777
N2O emission during nitrification/denitrification (ANOX1) |  | kg N2O/d |  |  | 0.011245 |  | 0.017495 |  | 0.01437 | 0.0044196 | 0.0062503
N2O emission during nitrification/denitrification (AER1) |  | kg N2O/d |  |  | 1.2001 |  | 1.9103 |  | 1.5552 | 0.50218 | 0.71019
N2O emission during nitrification/denitrification (AER2) |  | kg N2O/d |  |  | 0.55914 |  | 0.95093 |  | 0.75503 | 0.27703 | 0.39179
N2O emission during nitrification/denitrification (AER3) |  | kg N2O/d |  |  | 0.23503 |  | 0.4314 |  | 0.33322 | 0.13886 | 0.19637
N2O emission during nitrification/denitrification (total) |  | kg N2O/d |  |  | 2.0161 |  | 3.3265 |  | 2.6713 | 0.92661 | 1.3104

## Sheet2
Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load
--------------------------------------------- | --------------------------------------------- | --------------------------------------------- | --------------------------------------------- | --------------------------------------------- | --------------------------------------------- | ---------------------------------------------
Effluent average flow rate = 18061.3319 m3/d | Effluent average flow rate = 18061.3319 m3/d | Effluent average flow rate = 18061.3319 m3/d | Effluent average flow rate = 18061.3319 m3/d | Effluent average flow rate = 18061.1774 m3/d | Effluent average flow rate = 18061.1695 m3/d | Effluent average flow rate = 18061.1677 m3/d
Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3
Effluent average SS conc = 1.2287 g COD/m3 | Effluent average SS conc = 1.208 g COD/m3 | Effluent average SS conc = 1.2081 g COD/m3 | Effluent average SS conc = 1.2081 g COD/m3 | Effluent average SS conc = 1.2087 g COD/m3 | Effluent average SS conc = 1.2119 g COD/m3 | Effluent average SS conc = 1.2215 g COD/m3
Effluent average XI conc = 4.7314 g COD/m3 | Effluent average XI conc = 4.6921 g COD/m3 | Effluent average XI conc = 4.692 g COD/m3 | Effluent average XI conc = 4.692 g COD/m3 | Effluent average XI conc = 4.7035 g COD/m3 | Effluent average XI conc = 4.7007 g COD/m3 | Effluent average XI conc = 4.6962 g COD/m3
Effluent average XS conc = 0.21347 g COD/m3 | Effluent average XS conc = 0.21511 g COD/m3 | Effluent average XS conc = 0.21507 g COD/m3 | Effluent average XS conc = 0.21507 g COD/m3 | Effluent average XS conc = 0.2157 g COD/m3 | Effluent average XS conc = 0.21508 g COD/m3 | Effluent average XS conc = 0.22139 g COD/m3
Effluent average XBH conc = 9.5411 g COD/m3 | Effluent average XBH conc = 9.8003 g COD/m3 | Effluent average XBH conc = 9.8001 g COD/m3 | Effluent average XBH conc = 9.8001 g COD/m3 | Effluent average XBH conc = 9.8145 g COD/m3 | Effluent average XBH conc = 9.8119 g COD/m3 | Effluent average XBH conc = 9.8352 g COD/m3
Effluent average XBA1 conc = 0.51303 g COD/m3 | Effluent average XBA1 conc = 0.52311 g COD/m3 | Effluent average XBA1 conc = 0.52307 g COD/m3 | Effluent average XBA1 conc = 0.52307 g COD/m3 | Effluent average XBA1 conc = 0.52387 g COD/m3 | Effluent average XBA1 conc = 0.52312 g COD/m3 | Effluent average XBA1 conc = 0.51585 g COD/m3
Effluent average XP conc = 1.8024 g COD/m3 | Effluent average XP conc = 1.7213 g COD/m3 | Effluent average XP conc = 1.7213 g COD/m3 | Effluent average XP conc = 1.7213 g COD/m3 | Effluent average XP conc = 1.7236 g COD/m3 | Effluent average XP conc = 1.7231 g COD/m3 | Effluent average XP conc = 1.6912 g COD/m3
Effluent average SO conc = 3.6474 g (-COD)/m3 | Effluent average SO conc = 3.6043 g (-COD)/m3 | Effluent average SO conc = 3.6035 g (-COD)/m3 | Effluent average SO conc = 3.6035 g (-COD)/m3 | Effluent average SO conc = 3.596 g (-COD)/m3 | Effluent average SO conc = 3.5801 g (-COD)/m3 | Effluent average SO conc = 3.5476 g (-COD)/m3
Effluent average SNO3 conc = 14.3628 g N/m3 | Effluent average SNO3 conc = 14.2119 g N/m3 | Effluent average SNO3 conc = 14.2375 g N/m3 | Effluent average SNO3 conc = 14.2375 g N/m3 | Effluent average SNO3 conc = 14.2372 g N/m3 | Effluent average SNO3 conc = 14.7235 g N/m3 | Effluent average SNO3 conc = 14.9205 g N/m3
Effluent average SNH conc = 1.6635 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.5891 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.5908 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.5908 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.6016 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.6374 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.7265 g N/m3 (limit = 4 g N/m3)
Effluent average SND conc = 0.56392 g N/m3 | Effluent average SND conc = 0.55629 g N/m3 | Effluent average SND conc = 0.55624 g N/m3 | Effluent average SND conc = 0.55624 g N/m3 | Effluent average SND conc = 0.55649 g N/m3 | Effluent average SND conc = 0.55553 g N/m3 | Effluent average SND conc = 0.55713 g N/m3
Effluent average XND conc = 0.015767 g N/m3 | Effluent average XND conc = 0.015962 g N/m3 | Effluent average XND conc = 0.01596 g N/m3 | Effluent average XND conc = 0.01596 g N/m3 | Effluent average XND conc = 0.016004 g N/m3 | Effluent average XND conc = 0.015963 g N/m3 | Effluent average XND conc = 0.016357 g N/m3
Effluent average SALK conc = 3.8296 mol HCO3/m3 | Effluent average SALK conc = 3.8354 mol HCO3/m3 | Effluent average SALK conc = 3.834 mol HCO3/m3 | Effluent average SALK conc = 3.834 mol HCO3/m3 | Effluent average SALK conc = 3.8341 mol HCO3/m3 | Effluent average SALK conc = 3.806 mol HCO3/m3 | Effluent average SALK conc = 3.7995 mol HCO3/m3
Effluent average TSS conc = 12.7131 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8286 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8288 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8288 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8511 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8571 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8541 g SS/m3 (limit = 30 g SS/m3)
Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC
Effluent average SNO2 conc = 0.10928 g N/m3 | Effluent average SNO2 conc = 0.10495 g N/m3 | Effluent average SNO2 conc = 0.1011 g N/m3 | Effluent average SNO2 conc = 0.1011 g N/m3 | Effluent average SNO2 conc = 0.10206 g N/m3 | Effluent average SNO2 conc = 0.043797 g N/m3 | Effluent average SNO2 conc = 0.026941 g N/m3
Effluent average SNO conc = 0.0049457 g N/m3 | Effluent average SNO conc = 0.0048264 g N/m3 | Effluent average SNO conc = 0.0047105 g N/m3 | Effluent average SNO conc = 0.0047105 g N/m3 | Effluent average SNO conc = 0.0047473 g N/m3 | Effluent average SNO conc = 0.0026856 g N/m3 | Effluent average SNO conc = 0.0018406 g N/m3
Effluent average SN2O conc = 0.002591 g N/m3 | Effluent average SN2O conc = 0.0025654 g N/m3 | Effluent average SN2O conc = 0.0025051 g N/m3 | Effluent average SN2O conc = 0.0025051 g N/m3 | Effluent average SN2O conc = 0.0025244 g N/m3 | Effluent average SN2O conc = 0.001433 g N/m3 | Effluent average SN2O conc = 0.00097381 g N/m3
Effluent average SN2 conc = 13.3587 g N/m3 | Effluent average SN2 conc = 13.3606 g N/m3 | Effluent average SN2 conc = 13.3975 g N/m3 | Effluent average SN2 conc = 13.3975 g N/m3 | Effluent average SN2 conc = 13.3978 g N/m3 | Effluent average SN2 conc = 13.3924 g N/m3 | Effluent average SN2 conc = 13.3896 g N/m3
Effluent average XBA2 conc = 0.14944 g COD/m3 | Effluent average XBA2 conc = 0.15281 g COD/m3 | Effluent average XBA2 conc = 0.1535 g COD/m3 | Effluent average XBA2 conc = 0.1535 g COD/m3 | Effluent average XBA2 conc = 0.15372 g COD/m3 | Effluent average XBA2 conc = 0.16899 g COD/m3 | Effluent average XBA2 conc = 0.17907 g COD/m3
Effluent average Kjeldahl N conc = 3.5127 g N/m3 | Effluent average Kjeldahl N conc = 3.4471 g N/m3 | Effluent average Kjeldahl N conc = 3.4488 g N/m3 | Effluent average Kjeldahl N conc = 3.4488 g N/m3 | Effluent average Kjeldahl N conc = 3.4621 g N/m3 | Effluent average Kjeldahl N conc = 3.4977 g N/m3 | Effluent average Kjeldahl N conc = 3.5888 g N/m3
Effluent average total N conc = 17.9923 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 17.7713 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 17.7946 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 17.7946 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 17.8086 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 18.2691 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 18.539 g N/m3 (limit = 18 g N/m3)
Effluent average total COD conc = 48.1796 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3127 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3132 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3132 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3434 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3548 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3603 g COD/m3 (limit = 100 g COD/m3)
Effluent average BOD5 conc = 3.1219 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 3.1612 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 3.1613 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 3.1613 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 3.1657 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 3.169 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 3.1716 g/m3 (limit = 10 g/m3)
Effluent average load | Effluent average load | Effluent average load | Effluent average load | Effluent average load | Effluent average load | Effluent average load
--------------------- | --------------------- | --------------------- | --------------------- | --------------------- | --------------------- | ---------------------
Effluent average SI load = 541.84 kg COD/day | Effluent average SI load = 541.84 kg COD/day | Effluent average SI load = 541.84 kg COD/day | Effluent average SI load = 541.84 kg COD/day | Effluent average SI load = 541.8353 kg COD/day | Effluent average SI load = 541.8351 kg COD/day | Effluent average SI load = 541.835 kg COD/day
Effluent average SS load = 22.1925 kg COD/day | Effluent average SS load = 21.8178 kg COD/day | Effluent average SS load = 21.8204 kg COD/day | Effluent average SS load = 21.8204 kg COD/day | Effluent average SS load = 21.8297 kg COD/day | Effluent average SS load = 21.8887 kg COD/day | Effluent average SS load = 22.0611 kg COD/day
Effluent average XI load = 85.455 kg COD/day | Effluent average XI load = 84.7462 kg COD/day | Effluent average XI load = 84.7441 kg COD/day | Effluent average XI load = 84.7441 kg COD/day | Effluent average XI load = 84.9503 kg COD/day | Effluent average XI load = 84.8995 kg COD/day | Effluent average XI load = 84.8182 kg COD/day
Effluent average XS load = 3.8555 kg COD/day | Effluent average XS load = 3.8851 kg COD/day | Effluent average XS load = 3.8845 kg COD/day | Effluent average XS load = 3.8845 kg COD/day | Effluent average XS load = 3.8959 kg COD/day | Effluent average XS load = 3.8846 kg COD/day | Effluent average XS load = 3.9985 kg COD/day
Effluent average XBH load = 172.3257 kg COD/day | Effluent average XBH load = 177.0064 kg COD/day | Effluent average XBH load = 177.0037 kg COD/day | Effluent average XBH load = 177.0037 kg COD/day | Effluent average XBH load = 177.2607 kg COD/day | Effluent average XBH load = 177.2142 kg COD/day | Effluent average XBH load = 177.6347 kg COD/day
Effluent average XBA1 load = 9.266 kg COD/day | Effluent average XBA1 load = 9.448 kg COD/day | Effluent average XBA1 load = 9.4474 kg COD/day | Effluent average XBA1 load = 9.4474 kg COD/day | Effluent average XBA1 load = 9.4617 kg COD/day | Effluent average XBA1 load = 9.4482 kg COD/day | Effluent average XBA1 load = 9.3169 kg COD/day
Effluent average XP load = 32.5537 kg COD/day | Effluent average XP load = 31.0886 kg COD/day | Effluent average XP load = 31.0882 kg COD/day | Effluent average XP load = 31.0882 kg COD/day | Effluent average XP load = 31.1295 kg COD/day | Effluent average XP load = 31.1215 kg COD/day | Effluent average XP load = 30.5443 kg COD/day
Effluent average SO load = 65.8773 kg (-COD)/day | Effluent average SO load = 65.0977 kg (-COD)/day | Effluent average SO load = 65.0843 kg (-COD)/day | Effluent average SO load = 65.0843 kg (-COD)/day | Effluent average SO load = 64.9476 kg (-COD)/day | Effluent average SO load = 64.6604 kg (-COD)/day | Effluent average SO load = 64.0746 kg (-COD)/day
Effluent average SNO3 load = 259.412 kg N/day | Effluent average SNO3 load = 256.6857 kg N/day | Effluent average SNO3 load = 257.1475 kg N/day | Effluent average SNO3 load = 257.1475 kg N/day | Effluent average SNO3 load = 257.1413 kg N/day | Effluent average SNO3 load = 265.9235 kg N/day | Effluent average SNO3 load = 269.4812 kg N/day
Effluent average SNH load = 30.0442 kg N/day | Effluent average SNH load = 28.7009 kg N/day | Effluent average SNH load = 28.732 kg N/day | Effluent average SNH load = 28.732 kg N/day | Effluent average SNH load = 28.9276 kg N/day | Effluent average SNH load = 29.5732 kg N/day | Effluent average SNH load = 31.1827 kg N/day
Effluent average SND load = 10.1851 kg N/day | Effluent average SND load = 10.0473 kg N/day | Effluent average SND load = 10.0464 kg N/day | Effluent average SND load = 10.0464 kg N/day | Effluent average SND load = 10.0509 kg N/day | Effluent average SND load = 10.0335 kg N/day | Effluent average SND load = 10.0624 kg N/day
Effluent average XND load = 0.28477 kg N/day | Effluent average XND load = 0.2883 kg N/day | Effluent average XND load = 0.28826 kg N/day | Effluent average XND load = 0.28826 kg N/day | Effluent average XND load = 0.28906 kg N/day | Effluent average XND load = 0.2883 kg N/day | Effluent average XND load = 0.29543 kg N/day
Effluent average SALK load = 69.1685 kmol HCO3/day | Effluent average SALK load = 69.273 kmol HCO3/day | Effluent average SALK load = 69.2472 kmol HCO3/day | Effluent average SALK load = 69.2472 kmol HCO3/day | Effluent average SALK load = 69.2477 kmol HCO3/day | Effluent average SALK load = 68.7416 kmol HCO3/day | Effluent average SALK load = 68.6241 kmol HCO3/day
Effluent average TSS load = 229.6162 kg SS/day | Effluent average TSS load = 231.7008 kg SS/day | Effluent average TSS load = 231.7053 kg SS/day | Effluent average TSS load = 231.7053 kg SS/day | Effluent average TSS load = 232.1059 kg SS/day | Effluent average TSS load = 232.2151 kg SS/day | Effluent average TSS load = 232.16 kg SS/day
Effluent average SNO2 load = 1.9738 kg N/day | Effluent average SNO2 load = 1.8955 kg N/day | Effluent average SNO2 load = 1.826 kg N/day | Effluent average SNO2 load = 1.826 kg N/day | Effluent average SNO2 load = 1.8432 kg N/day | Effluent average SNO2 load = 0.79103 kg N/day | Effluent average SNO2 load = 0.48658 kg N/day
Effluent average SNO load = 0.089327 kg N/day | Effluent average SNO load = 0.087171 kg N/day | Effluent average SNO load = 0.085077 kg N/day | Effluent average SNO load = 0.085077 kg N/day | Effluent average SNO load = 0.085743 kg N/day | Effluent average SNO load = 0.048505 kg N/day | Effluent average SNO load = 0.033244 kg N/day
Effluent average SNO load = 0.046797 kg N/day | Effluent average SNO load = 0.046335 kg N/day | Effluent average SNO load = 0.045246 kg N/day | Effluent average SNO load = 0.045246 kg N/day | Effluent average SNO load = 0.045594 kg N/day | Effluent average SNO load = 0.025882 kg N/day | Effluent average SNO load = 0.017588 kg N/day
Effluent average SN2O load = 241.2758 kg N/day | Effluent average SN2O load = 241.31 kg N/day | Effluent average SN2O load = 241.9767 kg N/day | Effluent average SN2O load = 241.9767 kg N/day | Effluent average SN2O load = 241.9792 kg N/day | Effluent average SN2O load = 241.8824 kg N/day | Effluent average SN2O load = 241.8326 kg N/day
Effluent average SN2 load = 2.6991 kg COD/day | Effluent average SN2 load = 2.76 kg COD/day | Effluent average SN2 load = 2.7725 kg COD/day | Effluent average SN2 load = 2.7725 kg COD/day | Effluent average SN2 load = 2.7764 kg COD/day | Effluent average SN2 load = 3.0521 kg COD/day | Effluent average SN2 load = 3.2341 kg COD/day
Effluent average Kjeldahl N load = 63.4436 kg N/d | Effluent average Kjeldahl N load = 62.2591 kg N/d | Effluent average Kjeldahl N load = 62.2898 kg N/d | Effluent average Kjeldahl N load = 62.2898 kg N/d | Effluent average Kjeldahl N load = 62.5292 kg N/d | Effluent average Kjeldahl N load = 63.1717 kg N/d | Effluent average Kjeldahl N load = 64.8182 kg N/d
Effluent average total N load = 324.9656 kg N/d | Effluent average total N load = 320.9738 kg N/d | Effluent average total N load = 321.3937 kg N/d | Effluent average total N load = 321.3937 kg N/d | Effluent average total N load = 321.6451 kg N/d | Effluent average total N load = 329.9607 kg N/d | Effluent average total N load = 334.8368 kg N/d
Effluent average total COD load = 870.1875 kg COD/d | Effluent average total COD load = 872.5921 kg COD/d | Effluent average total COD load = 872.6007 kg COD/d | Effluent average total COD load = 872.6007 kg COD/d | Effluent average total COD load = 873.1395 kg COD/d | Effluent average total COD load = 873.344 kg COD/d | Effluent average total COD load = 873.4428 kg COD/d
Effluent average BOD5 load = 48.8989 kg BOD5/d | Effluent average BOD5 load = 49.945 kg BOD5/d | Effluent average BOD5 load = 49.9477 kg BOD5/d | Effluent average BOD5 load = 49.9477 kg BOD5/d | Effluent average BOD5 load = 50.0161 kg BOD5/d | Effluent average BOD5 load = 50.0777 kg BOD5/d | Effluent average BOD5 load = 50.2576 kg BOD5/d
Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load
-------------------------------------------------------- | -------------------------------------------------------- | -------------------------------------------------------- | -------------------------------------------------------- | -------------------------------------------------------- | -------------------------------------------------------- | --------------------------------------------------------
Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d
Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3
Sludge for disposal average SS conc = 1.2028 g COD/m3 | Sludge for disposal average SS conc = 1.1831 g COD/m3 | Sludge for disposal average SS conc = 1.1832 g COD/m3 | Sludge for disposal average SS conc = 1.1832 g COD/m3 | Sludge for disposal average SS conc = 1.1832 g COD/m3 | Sludge for disposal average SS conc = 1.1855 g COD/m3 | Sludge for disposal average SS conc = 1.1922 g COD/m3
Sludge for disposal average XI conc = 2242.0409 g COD/m3 | Sludge for disposal average XI conc = 2251.178 g COD/m3 | Sludge for disposal average XI conc = 2251.1798 g COD/m3 | Sludge for disposal average XI conc = 2251.1798 g COD/m3 | Sludge for disposal average XI conc = 2253.3258 g COD/m3 | Sludge for disposal average XI conc = 2253.4019 g COD/m3 | Sludge for disposal average XI conc = 2250.6331 g COD/m3
Sludge for disposal average XS conc = 99.3718 g COD/m3 | Sludge for disposal average XS conc = 101.3151 g COD/m3 | Sludge for disposal average XS conc = 101.302 g COD/m3 | Sludge for disposal average XS conc = 101.302 g COD/m3 | Sludge for disposal average XS conc = 101.2962 g COD/m3 | Sludge for disposal average XS conc = 101.0669 g COD/m3 | Sludge for disposal average XS conc = 102.603 g COD/m3
Sludge for disposal average XBH conc = 4531.3677 g COD/m3 | Sludge for disposal average XBH conc = 4705.8464 g COD/m3 | Sludge for disposal average XBH conc = 4705.8946 g COD/m3 | Sludge for disposal average XBH conc = 4705.8946 g COD/m3 | Sludge for disposal average XBH conc = 4705.781 g COD/m3 | Sludge for disposal average XBH conc = 4707.5006 g COD/m3 | Sludge for disposal average XBH conc = 4718.4697 g COD/m3
Sludge for disposal average XBA1 conc = 243.116 g COD/m3 | Sludge for disposal average XBA1 conc = 250.8701 g COD/m3 | Sludge for disposal average XBA1 conc = 250.8612 g COD/m3 | Sludge for disposal average XBA1 conc = 250.8612 g COD/m3 | Sludge for disposal average XBA1 conc = 250.8751 g COD/m3 | Sludge for disposal average XBA1 conc = 250.6766 g COD/m3 | Sludge for disposal average XBA1 conc = 247.151 g COD/m3
Sludge for disposal average XP conc = 852.1393 g COD/m3 | Sludge for disposal average XP conc = 825.1769 g COD/m3 | Sludge for disposal average XP conc = 825.1857 g COD/m3 | Sludge for disposal average XP conc = 825.1857 g COD/m3 | Sludge for disposal average XP conc = 825.0903 g COD/m3 | Sludge for disposal average XP conc = 825.4043 g COD/m3 | Sludge for disposal average XP conc = 809.9203 g COD/m3
Sludge for disposal average SO conc = 3.8494 g (-COD)/m3 | Sludge for disposal average SO conc = 3.8101 g (-COD)/m3 | Sludge for disposal average SO conc = 3.8095 g (-COD)/m3 | Sludge for disposal average SO conc = 3.8095 g (-COD)/m3 | Sludge for disposal average SO conc = 3.8085 g (-COD)/m3 | Sludge for disposal average SO conc = 3.7939 g (-COD)/m3 | Sludge for disposal average SO conc = 3.7613 g (-COD)/m3
Sludge for disposal average SNO3 conc = 14.5001 g N/m3 | Sludge for disposal average SNO3 conc = 14.3432 g N/m3 | Sludge for disposal average SNO3 conc = 14.3679 g N/m3 | Sludge for disposal average SNO3 conc = 14.3679 g N/m3 | Sludge for disposal average SNO3 conc = 14.3701 g N/m3 | Sludge for disposal average SNO3 conc = 14.842 g N/m3 | Sludge for disposal average SNO3 conc = 15.0413 g N/m3
Sludge for disposal average SNH conc = 1.4071 g N/m3 | Sludge for disposal average SNH conc = 1.3408 g N/m3 | Sludge for disposal average SNH conc = 1.3423 g N/m3 | Sludge for disposal average SNH conc = 1.3423 g N/m3 | Sludge for disposal average SNH conc = 1.3453 g N/m3 | Sludge for disposal average SNH conc = 1.3764 g N/m3 | Sludge for disposal average SNH conc = 1.4568 g N/m3
Sludge for disposal average SND conc = 0.55449 g N/m3 | Sludge for disposal average SND conc = 0.54734 g N/m3 | Sludge for disposal average SND conc = 0.54729 g N/m3 | Sludge for disposal average SND conc = 0.54729 g N/m3 | Sludge for disposal average SND conc = 0.54733 g N/m3 | Sludge for disposal average SND conc = 0.5464 g N/m3 | Sludge for disposal average SND conc = 0.54727 g N/m3
Sludge for disposal average XND conc = 7.3628 g N/m3 | Sludge for disposal average XND conc = 7.5412 g N/m3 | Sludge for disposal average XND conc = 7.5403 g N/m3 | Sludge for disposal average XND conc = 7.5403 g N/m3 | Sludge for disposal average XND conc = 7.5407 g N/m3 | Sludge for disposal average XND conc = 7.5259 g N/m3 | Sludge for disposal average XND conc = 7.6234 g N/m3
Sludge for disposal average SALK conc = 3.808 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8147 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8133 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8133 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8128 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.7845 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.7769 mol HCO3/m3
Sludge for disposal average TSS conc = 6029.3437 g SS/m3 | Sludge for disposal average TSS conc = 6155.9454 g SS/m3 | Sludge for disposal average TSS conc = 6156.2193 g SS/m3 | Sludge for disposal average TSS conc = 6156.2193 g SS/m3 | Sludge for disposal average TSS conc = 6157.6757 g SS/m3 | Sludge for disposal average TSS conc = 6164.358 g SS/m3 | Sludge for disposal average TSS conc = 6160.9237 g SS/m3
Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC
Sludge for disposal average SNO2 conc = 0.085892 g N/m3 | Sludge for disposal average SNO2 conc = 0.08219 g N/m3 | Sludge for disposal average SNO2 conc = 0.079203 g N/m3 | Sludge for disposal average SNO2 conc = 0.079203 g N/m3 | Sludge for disposal average SNO2 conc = 0.07953 g N/m3 | Sludge for disposal average SNO2 conc = 0.034915 g N/m3 | Sludge for disposal average SNO2 conc = 0.022222 g N/m3
Sludge for disposal average SNO conc = 0.0040165 g N/m3 | Sludge for disposal average SNO conc = 0.0038997 g N/m3 | Sludge for disposal average SNO conc = 0.0038062 g N/m3 | Sludge for disposal average SNO conc = 0.0038062 g N/m3 | Sludge for disposal average SNO conc = 0.0038173 g N/m3 | Sludge for disposal average SNO conc = 0.0021891 g N/m3 | Sludge for disposal average SNO conc = 0.0015396 g N/m3
Sludge for disposal average SN2O conc = 0.0021152 g N/m3 | Sludge for disposal average SN2O conc = 0.0020823 g N/m3 | Sludge for disposal average SN2O conc = 0.0020332 g N/m3 | Sludge for disposal average SN2O conc = 0.0020332 g N/m3 | Sludge for disposal average SN2O conc = 0.002039 g N/m3 | Sludge for disposal average SN2O conc = 0.0011698 g N/m3 | Sludge for disposal average SN2O conc = 0.00081455 g N/m3
Sludge for disposal average SN2 conc = 13.3549 g N/m3 | Sludge for disposal average SN2 conc = 13.3565 g N/m3 | Sludge for disposal average SN2 conc = 13.3907 g N/m3 | Sludge for disposal average SN2 conc = 13.3907 g N/m3 | Sludge for disposal average SN2 conc = 13.3908 g N/m3 | Sludge for disposal average SN2 conc = 13.3862 g N/m3 | Sludge for disposal average SN2 conc = 13.3839 g N/m3
Sludge for disposal average XBA2 conc = 71.0892 g COD/m3 | Sludge for disposal average XBA2 conc = 73.5408 g COD/m3 | Sludge for disposal average XBA2 conc = 73.869 g COD/m3 | Sludge for disposal average XBA2 conc = 73.869 g COD/m3 | Sludge for disposal average XBA2 conc = 73.8659 g COD/m3 | Sludge for disposal average XBA2 conc = 81.0936 g COD/m3 | Sludge for disposal average XBA2 conc = 85.788 g COD/m3
Sludge for disposal average Kjeldahl N conc = 615.9598 g N/m3 | Sludge for disposal average Kjeldahl N conc = 631.0252 g N/m3 | Sludge for disposal average Kjeldahl N conc = 631.0777 g N/m3 | Sludge for disposal average Kjeldahl N conc = 631.0777 g N/m3 | Sludge for disposal average Kjeldahl N conc = 631.1951 g N/m3 | Sludge for disposal average Kjeldahl N conc = 632.4199 g N/m3 | Sludge for disposal average Kjeldahl N conc = 632.829 g N/m3
Sludge for disposal average total N conc = 630.552 g N/m3 | Sludge for disposal average total N conc = 645.4565 g N/m3 | Sludge for disposal average total N conc = 645.5307 g N/m3 | Sludge for disposal average total N conc = 645.5307 g N/m3 | Sludge for disposal average total N conc = 645.6505 g N/m3 | Sludge for disposal average total N conc = 647.3002 g N/m3 | Sludge for disposal average total N conc = 647.8949 g N/m3
Sludge for disposal average total COD conc = 8070.3277 g COD/m3 | Sludge for disposal average total COD conc = 8239.1103 g COD/m3 | Sludge for disposal average total COD conc = 8239.4756 g COD/m3 | Sludge for disposal average total COD conc = 8239.4756 g COD/m3 | Sludge for disposal average total COD conc = 8241.4175 g COD/m3 | Sludge for disposal average total COD conc = 8250.3294 g COD/m3 | Sludge for disposal average total COD conc = 8245.7571 g COD/m3
Sludge for disposal average BOD5 conc = 1139.6254 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1182.5837 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1182.665 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1182.665 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1182.6399 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1184.5954 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1187.7728 g BOD5/m3
Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load
-------------------------------- | -------------------------------- | -------------------------------- | -------------------------------- | -------------------------------- | -------------------------------- | --------------------------------
Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day
Sludge for disposal average SS load = 0.46307 kg COD/day | Sludge for disposal average SS load = 0.4555 kg COD/day | Sludge for disposal average SS load = 0.45554 kg COD/day | Sludge for disposal average SS load = 0.45554 kg COD/day | Sludge for disposal average SS load = 0.45552 kg COD/day | Sludge for disposal average SS load = 0.45641 kg COD/day | Sludge for disposal average SS load = 0.45898 kg COD/day
Sludge for disposal average XI load = 863.1858 kg COD/day | Sludge for disposal average XI load = 866.7035 kg COD/day | Sludge for disposal average XI load = 866.7042 kg COD/day | Sludge for disposal average XI load = 866.7042 kg COD/day | Sludge for disposal average XI load = 867.5304 kg COD/day | Sludge for disposal average XI load = 867.5597 kg COD/day | Sludge for disposal average XI load = 866.4937 kg COD/day
Sludge for disposal average XS load = 38.2581 kg COD/day | Sludge for disposal average XS load = 39.0063 kg COD/day | Sludge for disposal average XS load = 39.0013 kg COD/day | Sludge for disposal average XS load = 39.0013 kg COD/day | Sludge for disposal average XS load = 38.9991 kg COD/day | Sludge for disposal average XS load = 38.9108 kg COD/day | Sludge for disposal average XS load = 39.5021 kg COD/day
Sludge for disposal average XBH load = 1744.5766 kg COD/day | Sludge for disposal average XBH load = 1811.7508 kg COD/day | Sludge for disposal average XBH load = 1811.7694 kg COD/day | Sludge for disposal average XBH load = 1811.7694 kg COD/day | Sludge for disposal average XBH load = 1811.7257 kg COD/day | Sludge for disposal average XBH load = 1812.3877 kg COD/day | Sludge for disposal average XBH load = 1816.6108 kg COD/day
Sludge for disposal average XBA load = 93.5996 kg COD/day | Sludge for disposal average XBA load = 96.585 kg COD/day | Sludge for disposal average XBA load = 96.5816 kg COD/day | Sludge for disposal average XBA load = 96.5816 kg COD/day | Sludge for disposal average XBA load = 96.5869 kg COD/day | Sludge for disposal average XBA load = 96.5105 kg COD/day | Sludge for disposal average XBA load = 95.1531 kg COD/day
Sludge for disposal average XP load = 328.0736 kg COD/day | Sludge for disposal average XP load = 317.6931 kg COD/day | Sludge for disposal average XP load = 317.6965 kg COD/day | Sludge for disposal average XP load = 317.6965 kg COD/day | Sludge for disposal average XP load = 317.6598 kg COD/day | Sludge for disposal average XP load = 317.7807 kg COD/day | Sludge for disposal average XP load = 311.8193 kg COD/day
Sludge for disposal average SO load = 1.482 kg (-COD)/day | Sludge for disposal average SO load = 1.4669 kg (-COD)/day | Sludge for disposal average SO load = 1.4666 kg (-COD)/day | Sludge for disposal average SO load = 1.4666 kg (-COD)/day | Sludge for disposal average SO load = 1.4663 kg (-COD)/day | Sludge for disposal average SO load = 1.4606 kg (-COD)/day | Sludge for disposal average SO load = 1.4481 kg (-COD)/day
Sludge for disposal average SNO3 load = 5.5826 kg N/day | Sludge for disposal average SNO3 load = 5.5221 kg N/day | Sludge for disposal average SNO3 load = 5.5317 kg N/day | Sludge for disposal average SNO3 load = 5.5317 kg N/day | Sludge for disposal average SNO3 load = 5.5325 kg N/day | Sludge for disposal average SNO3 load = 5.7142 kg N/day | Sludge for disposal average SNO3 load = 5.7909 kg N/day
Sludge for disposal average SNH load = 0.54173 kg N/day | Sludge for disposal average SNH load = 0.51621 kg N/day | Sludge for disposal average SNH load = 0.51678 kg N/day | Sludge for disposal average SNH load = 0.51678 kg N/day | Sludge for disposal average SNH load = 0.51793 kg N/day | Sludge for disposal average SNH load = 0.5299 kg N/day | Sludge for disposal average SNH load = 0.56085 kg N/day
Sludge for disposal average SND load = 0.21348 kg N/day | Sludge for disposal average SND load = 0.21072 kg N/day | Sludge for disposal average SND load = 0.21071 kg N/day | Sludge for disposal average SND load = 0.21071 kg N/day | Sludge for disposal average SND load = 0.21072 kg N/day | Sludge for disposal average SND load = 0.21036 kg N/day | Sludge for disposal average SND load = 0.2107 kg N/day
Sludge for disposal average XND load = 2.8347 kg N/day | Sludge for disposal average XND load = 2.9034 kg N/day | Sludge for disposal average XND load = 2.903 kg N/day | Sludge for disposal average XND load = 2.903 kg N/day | Sludge for disposal average XND load = 2.9032 kg N/day | Sludge for disposal average XND load = 2.8975 kg N/day | Sludge for disposal average XND load = 2.935 kg N/day
Sludge for disposal average SALK load = 1.4661 kmol HCO3/day | Sludge for disposal average SALK load = 1.4687 kmol HCO3/day | Sludge for disposal average SALK load = 1.4681 kmol HCO3/day | Sludge for disposal average SALK load = 1.4681 kmol HCO3/day | Sludge for disposal average SALK load = 1.4679 kmol HCO3/day | Sludge for disposal average SALK load = 1.457 kmol HCO3/day | Sludge for disposal average SALK load = 1.4541 kmol HCO3/day
Sludge for disposal average TSS load = 2321.2973 kg SS/day | Sludge for disposal average TSS load = 2370.039 kg SS/day | Sludge for disposal average TSS load = 2370.1444 kg SS/day | Sludge for disposal average TSS load = 2370.1444 kg SS/day | Sludge for disposal average TSS load = 2370.7052 kg SS/day | Sludge for disposal average TSS load = 2373.2778 kg SS/day | Sludge for disposal average TSS load = 2371.9556 kg SS/day
Sludge for disposal average SNO2 load = 0.033068 kg N/day | Sludge for disposal average SNO2 load = 0.031643 kg N/day | Sludge for disposal average SNO2 load = 0.030493 kg N/day | Sludge for disposal average SNO2 load = 0.030493 kg N/day | Sludge for disposal average SNO2 load = 0.030619 kg N/day | Sludge for disposal average SNO2 load = 0.013442 kg N/day | Sludge for disposal average SNO2 load = 0.0085554 kg N/day
Sludge for disposal average SNO load = 0.0015463 kg N/day | Sludge for disposal average SNO load = 0.0015014 kg N/day | Sludge for disposal average SNO load = 0.0014654 kg N/day | Sludge for disposal average SNO load = 0.0014654 kg N/day | Sludge for disposal average SNO load = 0.0014696 kg N/day | Sludge for disposal average SNO load = 0.0008428 kg N/day | Sludge for disposal average SNO load = 0.00059273 kg N/day
Sludge for disposal average SN2O load = 0.00081437 kg N/day | Sludge for disposal average SN2O load = 0.0008017 kg N/day | Sludge for disposal average SN2O load = 0.00078278 kg N/day | Sludge for disposal average SN2O load = 0.00078278 kg N/day | Sludge for disposal average SN2O load = 0.00078502 kg N/day | Sludge for disposal average SN2O load = 0.00045036 kg N/day | Sludge for disposal average SN2O load = 0.0003136 kg N/day
Sludge for disposal average SN2 load = 5.1416 kg N/day | Sludge for disposal average SN2 load = 5.1423 kg N/day | Sludge for disposal average SN2 load = 5.1554 kg N/day | Sludge for disposal average SN2 load = 5.1554 kg N/day | Sludge for disposal average SN2 load = 5.1555 kg N/day | Sludge for disposal average SN2 load = 5.1537 kg N/day | Sludge for disposal average SN2 load = 5.1528 kg N/day
Sludge for disposal average XBA2 load = 27.3693 kg N/day | Sludge for disposal average XBA2 load = 28.3132 kg N/day | Sludge for disposal average XBA2 load = 28.4396 kg N/day | Sludge for disposal average XBA2 load = 28.4396 kg N/day | Sludge for disposal average XBA2 load = 28.4384 kg N/day | Sludge for disposal average XBA2 load = 31.221 kg N/day | Sludge for disposal average XBA2 load = 33.0284 kg N/day
Sludge for disposal average Kjeldahl N load = 235.5024 kg N/d | Sludge for disposal average Kjeldahl N load = 241.2459 kg N/d | Sludge for disposal average Kjeldahl N load = 241.2586 kg N/d | Sludge for disposal average Kjeldahl N load = 241.2586 kg N/d | Sludge for disposal average Kjeldahl N load = 241.3038 kg N/d | Sludge for disposal average Kjeldahl N load = 241.6084 kg N/d | Sludge for disposal average Kjeldahl N load = 241.6575 kg N/d
Sludge for disposal average total N load = 241.1203 kg N/d | Sludge for disposal average total N load = 246.802 kg N/d | Sludge for disposal average total N load = 246.8229 kg N/d | Sludge for disposal average total N load = 246.8229 kg N/d | Sludge for disposal average total N load = 246.8691 kg N/d | Sludge for disposal average total N load = 247.3373 kg N/d | Sludge for disposal average total N load = 247.4578 kg N/d
Sludge for disposal average total COD load = 3107.0762 kg COD/d | Sludge for disposal average total COD load = 3172.0575 kg COD/d | Sludge for disposal average total COD load = 3172.1981 kg COD/d | Sludge for disposal average total COD load = 3172.1981 kg COD/d | Sludge for disposal average total COD load = 3172.9457 kg COD/d | Sludge for disposal average total COD load = 3176.3768 kg COD/d | Sludge for disposal average total COD load = 3174.6165 kg COD/d
Sludge for disposal average BOD5 load = 438.7558 kg BOD5/d | Sludge for disposal average BOD5 load = 455.2947 kg BOD5/d | Sludge for disposal average BOD5 load = 455.326 kg BOD5/d | Sludge for disposal average BOD5 load = 455.326 kg BOD5/d | Sludge for disposal average BOD5 load = 455.3164 kg BOD5/d | Sludge for disposal average BOD5 load = 456.0692 kg BOD5/d | Sludge for disposal average BOD5 load = 457.2925 kg BOD5/d
Other effluent quality variables | Other effluent quality variables | Other effluent quality variables | Other effluent quality variables | Other effluent quality variables | Other effluent quality variables | Other effluent quality variables
-------------------------------- | -------------------------------- | -------------------------------- | -------------------------------- | -------------------------------- | -------------------------------- | --------------------------------
Influent Quality Index (IQI) = 52174.9257 kg poll.units/d | Influent Quality Index (IQI) = 52174.9257 kg poll.units/d | Influent Quality Index (IQI) = 52174.9257 kg poll.units/d | Influent Quality Index (IQI) = 52174.9257 kg poll.units/d | Influent Quality Index (IQI) = 52174.9256 kg poll.units/d | Influent Quality Index (IQI) = 52174.9256 kg poll.units/d | Influent Quality Index (IQI) = 52174.9256 kg poll.units/d
Effluent Quality Index (EQI) = 5953.7576 kg poll.units/d | Effluent Quality Index (EQI) = 5897.9833 kg poll.units/d | Effluent Quality Index (EQI) = 5902.7876 kg poll.units/d | Effluent Quality Index (EQI) = 5902.7876 kg poll.units/d | Effluent Quality Index (EQI) = 5911.5754 kg poll.units/d | Effluent Quality Index (EQI) = 6007.4128 kg poll.units/d | Effluent Quality Index (EQI) = 6088.7156 kg poll.units/d
Sludge production for disposal = 39256.3644 kg SS | Sludge production for disposal = 39905.5208 kg SS | Sludge production for disposal = 16591.011 kg SS | Sludge production for disposal = 16591.011 kg SS | Sludge production for disposal = 16594.9361 kg SS | Sludge production for disposal = 16612.9447 kg SS | Sludge production for disposal = 16603.6895 kg SS
Average sludge production for disposal per day = 5608.0521 kg SS/d | Average sludge production for disposal per day = 5700.7887 kg SS/d | Average sludge production for disposal per day = 2370.1444 kg SS/d | Average sludge production for disposal per day = 2370.1444 kg SS/d | Average sludge production for disposal per day = 2370.7052 kg SS/d | Average sludge production for disposal per day = 2373.2778 kg SS/d | Average sludge production for disposal per day = 2371.9556 kg SS/d
Sludge production released into effluent = 1607.3137 kg SS | Sludge production released into effluent = 1621.9055 kg SS | Sludge production released into effluent = 1621.9369 kg SS | Sludge production released into effluent = 1621.9369 kg SS | Sludge production released into effluent = 1624.741 kg SS | Sludge production released into effluent = 1625.5057 kg SS | Sludge production released into effluent = 1625.12 kg SS
Average sludge production released into effluent per day = 229.6162 kg SS/d | Average sludge production released into effluent per day = 231.7008 kg SS/d | Average sludge production released into effluent per day = 231.7053 kg SS/d | Average sludge production released into effluent per day = 231.7053 kg SS/d | Average sludge production released into effluent per day = 232.1059 kg SS/d | Average sludge production released into effluent per day = 232.2151 kg SS/d | Average sludge production released into effluent per day = 232.16 kg SS/d
Total sludge production = 40863.678 kg SS | Total sludge production = 41527.4262 kg SS | Total sludge production = 18212.9479 kg SS | Total sludge production = 18212.9479 kg SS | Total sludge production = 18219.6772 kg SS | Total sludge production = 18238.4504 kg SS | Total sludge production = 18228.8094 kg SS
Total average sludge production per day = 5837.6683 kg SS/d | Total average sludge production per day = 5932.4895 kg SS/d | Total average sludge production per day = 2601.8497 kg SS/d | Total average sludge production per day = 2601.8497 kg SS/d | Total average sludge production per day = 2602.811 kg SS/d | Total average sludge production per day = 2605.4929 kg SS/d | Total average sludge production per day = 2604.1156 kg SS/d
Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d
Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d
Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d
Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d
Operational Cost Index | Operational Cost Index | Operational Cost Index | Operational Cost Index | Operational Cost Index | Operational Cost Index | Operational Cost Index
---------------------- | ---------------------- | ---------------------- | ---------------------- | ---------------------- | ---------------------- | ----------------------
Sludge production cost index = 16824.1562 | Sludge production cost index = 17102.366 | Sludge production cost index = 7110.4333 | Sludge production cost index = 7110.4333 | Sludge production cost index = 7112.1155 | Sludge production cost index = 7119.8334 | Sludge production cost index = 7115.8669
Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778
Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17
Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0
Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240
Total Operational Cost Index (OCI) = 21735.7039 | Total Operational Cost Index (OCI) = 22013.9138 | Total Operational Cost Index (OCI) = 12021.9811 | Total Operational Cost Index (OCI) = 12021.9811 | Total Operational Cost Index (OCI) = 12023.6633 | Total Operational Cost Index (OCI) = 12031.3812 | Total Operational Cost Index (OCI) = 12027.4147
N2O Emissions | N2O Emissions | N2O Emissions | N2O Emissions | N2O Emissions | N2O Emissions | N2O Emissions
------------------- | ------------------- | ------------------- | ------------------- | ------------------- | ------------------- | -------------------
N2O emission during nitrification/denitrification (ANOX1) = 0.010872 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010846 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010835 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010835 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010835 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010644 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.01053 kg N2O/d
N2O emission during nitrification/denitrification (ANOX1) = 0.011226 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.011163 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.011167 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.011167 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.011167 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.011242 kg N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.011245 kg N2O/d
N2O emission during nitrification/denitrification (AER1) = 2.0247 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 2.0785 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 2.0523 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 2.0523 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 2.0542 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.5307 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.2001 kg N2O/d
N2O emission during nitrification/denitrification (AER2) = 1.2546 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 1.2583 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 1.2326 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 1.2326 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 1.2348 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.7788 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.55914 kg N2O/d
N2O emission during nitrification/denitrification (AER3) = 0.60701 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.5977 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.58367 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.58367 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.58548 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.33675 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.23503 kg N2O/d
N2O emission during nitrification/denitrification (total) = 3.9084 kg N2O/d | N2O emission during nitrification/denitrification (total) = 3.9565 kg N2O/d | N2O emission during nitrification/denitrification (total) = 3.8906 kg N2O/d | N2O emission during nitrification/denitrification (total) = 3.8906 kg N2O/d | N2O emission during nitrification/denitrification (total) = 3.8965 kg N2O/d | N2O emission during nitrification/denitrification (total) = 2.6681 kg N2O/d | N2O emission during nitrification/denitrification (total) = 2.0161 kg N2O/d
Effluent violations |  | Effluent violations | Effluent violations | Effluent violations | Effluent violations | Effluent violations
------------------- |  | ------------------- | ------------------- | ------------------- | ------------------- | -------------------
The maximum effluent ammonia nitrogen level (4 g N/m3) was violated |  | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated
during 0.72917 days, i.e. 10.4167% of the operating time. |  | during 0.6875 days, i.e. 9.8214% of the operating time. | during 0.6875 days, i.e. 9.8214% of the operating time. | during 0.6875 days, i.e. 9.8214% of the operating time. | during 0.69792 days, i.e. 9.9702% of the operating time. | during 0.76042 days, i.e. 10.8631% of the operating time.
The limit was violated at 5 different occasions. |  | The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions.
***** Plant evaluation of BSM2 system successfully finished ***** |  | ***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished *****
End time (hour:min:sec) = 16 13 12 |  | End time (hour:min:sec) = 17 23 8 | End time (hour:min:sec) = 14 56 5 | End time (hour:min:sec) = 12 30 25 | End time (hour:min:sec) = 17 28 16 | End time (hour:min:sec) = 15 11 48