## BSM2 OL (1 year)
Ring test BSM 1G |  | Openloop
Model component tested: | COMPLETE BSM1G | STATUS: | Integrated system | Dynamic | Openloop
See detailed specifications at the end of this sheet!
Test of BSM1G for full dynamics in openloop based on the finalised BSM2 and finalised evaluation criteria
Simulation procedure: simulate to steady state using CONSTANT INFLUENT and use final state variable values for initial values for dynamic simulation.
Run full 14 days simulation using input file from BSM web site and base evaluation on the last 7 days, i.e. from beginning of day 7.
Evaluation is based on data every 15 minutes and uses zero-order hold (forward Euler) for integration between measurements.
PLANT EVALUATION 1 YEAR (364 DAYS)
Effluent average concentrations based on load, including bypass
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Effluent average flow rate |  | m3/d |  |  | 18061.3319 |  |  |  | 18061.3319 | #DIV/0! | 0
Effluent average SI concentration |  | g COD/m3 |  |  | 30 |  |  |  | 30 | #DIV/0! | 0
Effluent average SS concentration |  | g COD/m3 |  |  | 1.2287 |  |  |  | 1.2287 | #DIV/0! | 0
Effluent average XI concentration |  | g COD/m3 |  |  | 4.7314 |  |  |  | 4.7314 | #DIV/0! | 0
Effluent average XS concentration |  | g COD/m3 |  |  | 0.21347 |  |  |  | 0.21347 | #DIV/0! | 0
Effluent average XBH concentration |  | g COD/m3 |  |  | 9.5411 |  |  |  | 9.5411 | #DIV/0! | 0
Effluent average XBA1 concentration |  | g COD/m3 |  |  | 0.51303 |  |  |  | 0.51303 | #DIV/0! | 0
Effluent average XP concentration |  | g COD/m3 |  |  | 1.8024 |  |  |  | 1.8024 | #DIV/0! | 0
Effluent average SO concentration |  | g -COD/m3 |  |  | 3.6474 |  |  |  | 3.6474 | #DIV/0! | 0
Effluent average SNO3 concentration |  | g N/m3 |  |  | 14.3628 |  |  |  | 14.3628 | #DIV/0! | 0
Effluent average SNH concentration (limit = 4 g N/m3) |  | g N/m3 |  |  | 1.6635 |  |  |  | 1.6635 | #DIV/0! | 0
Effluent average SND concentration |  | g N/m3 |  |  | 0.56392 |  |  |  | 0.56392 | #DIV/0! | 0
Effluent average XND concentration |  | g N/m3 |  |  | 0.015767 |  |  |  | 0.015767 | #DIV/0! | 0
Effluent average SALK concentration |  | mol HCO3-/m3 |  |  | 3.8296 |  |  |  | 3.8296 | #DIV/0! | 0
Effluent average TSS concentration (limit = 30 g SS/m3) |  | g/m3 |  |  | 12.7131 |  |  |  | 12.7131 | #DIV/0! | 0
Effluent average Temperature |  | deg C |  |  | 15 |  |  |  | 15 | #DIV/0! | 0
Effluent average SNO2 conc |  | g N/m3 |  |  | 0.10928
Effluent average SNO conc |  | g N/m3 |  |  | 0.0049457
Effluent average SN2O conc |  | g N/m3 |  |  | 0.002591
Effluent average SN2 conc |  | g N/m3 |  |  | 13.3587
Effluent average XBA2 conc |  | g COD/m3 |  |  | 0.14944 |  |  |  | 0.14944 | #DIV/0! | 0
Effluent average Kjeldahl N conc |  | g N/m3 |  |  | 3.5127
Effluent average total N concentration (limit = 18 g N/l) |  | g N/m3 |  |  | 17.9923 |  |  |  | 17.9923 | #DIV/0! | 0
Effluent average total COD concentration (limit = 100 g COD/m3) |  | g COD/m3 |  |  | 48.1796 |  |  |  | 48.1796 | #DIV/0! | 0
Effluent average BOD5 concentration (limit = 10 g/m3) |  | g/m3 |  |  | 3.1219 |  |  |  | 3.1219 | #DIV/0! | 0
Effluent average load, including bypass
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Effluent average SI load |  | kg COD/day |  | 0 | 541.84 |  |  |  | 270.92 | 383.1387 | 541.84
Effluent average SS load |  | kg COD/day |  | 0 | 22.1925 |  |  |  | 11.0962 | 15.6925 | 22.1925
Effluent average XI load |  | kg COD/day |  | 0 | 85.455 |  |  |  | 42.7275 | 60.4258 | 85.455
Effluent average XS load |  | kg COD/day |  | 0 | 3.8555 |  |  |  | 1.9278 | 2.7263 | 3.8555
Effluent average XBH load |  | kg COD/day |  | 0 | 172.3257 |  |  |  | 86.1629 | 121.8527 | 172.3257
Effluent average XBA load |  | kg COD/day |  | 0 | 9.266 |  |  |  | 4.633 | 6.5521 | 9.266
Effluent average XP load |  | kg COD/day |  | 0 | 32.5537 |  |  |  | 16.2768 | 23.0189 | 32.5537
Effluent average SO load |  | kg -COD/day |  | 0 | 65.8773 |  |  |  | 32.9387 | 46.5823 | 65.8773
Effluent average SNO load |  | kg N/day |  | 0 | 259.412 |  |  |  | 129.706 | 183.432 | 259.412
Effluent average SNH load |  | kg N/day |  | 0 | 30.0442 |  |  |  | 15.0221 | 21.2445 | 30.0442
Effluent average SND load |  | kg N/day |  | 0 | 10.1851 |  |  |  | 5.0926 | 7.202 | 10.1851
Effluent average XND load |  | kg N/day |  | 0 | 0.28477 |  |  |  | 0.14239 | 0.20136 | 0.28477
Effluent average SALK load |  | kmol HCO3-/day |  | 0 | 69.1685 |  |  |  | 34.5842 | 48.9095 | 69.1685
Effluent average TSS load |  | kg/day |  | 0 | 229.6162 |  |  |  | 114.8081 | 162.3632 | 229.6162
Effluent average SNO2 load |  | kg N/day |  |  | 1.9738
Effluent average SNO load |  | kg N/day |  |  | 0.089327
Effluent average SN2O load |  | kg N/day |  |  | 0.046797
Effluent average SN2 load |  | kg N/day |  |  | 241.2758
Effluent average XBA2 load |  | kg COD/day |  |  | 2.6991
Effluent average Kjeldahl N load |  | kg N/day |  | 0 | 63.4436 |  |  |  | 31.7218 | 44.8614 | 63.4436
Effluent average total N load |  | kg N/day |  | 0 | 324.9656 |  |  |  | 162.4828 | 229.7854 | 324.9656
Effluent average total COD load |  | kg COD/day |  | 0 | 870.1875 |  |  |  | 435.0938 | 615.3155 | 870.1875
Effluent average BOD5 load |  | kg/day |  | 0 | 48.8989 |  |  |  | 24.4494 | 34.5767 | 48.8989
Other output quality variables
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Influent quality (I.Q.) index |  | kg poll.units/day |  | 74700 | 52174.9257 |  |  |  | 63437.4628 | 15927.6328 | 22525.0743
Effluent quality (E.Q.) index |  | kg poll.units/day |  | 5660 | 5953.7576 |  |  |  | 5806.8788 | 207.718 | 293.7576
Average sludge production for disposal per day |  | kg SS/day |  | 2646 | 5608.0521 |  |  |  | 4127.0261 | 2094.4871 | 2962.0521
Average sludge production released into effluent per day |  | kg SS/day |  | 325 | 1607.3137 |  |  |  | 966.1568 | 906.7327 | 1282.3137
Total average sludge production per day |  | kg SS/day |  | 2971 | 5837.6683 |  |  |  | 4404.3342 | 2027.0406 | 2866.6683
'Energy' related variables
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Average aeration energy |  | kWh/d |  | 4000 | 4283.3778 |  |  |  | 4141.6889 | 200.3784 | 283.3778
Average pumping energy |  | kWh/d |  | 440.9 | 388.17 |  |  |  | 414.535 | 37.2857 | 52.73
Average carbon source dosage |  | kg COD/day |  | 800 | 0 |  |  |  | 400 | 565.6854 | 800
Average mixing energy |  | kWh/d |  | 768 | 240 |  |  |  | 504 | 373.3524 | 528
Operational cost index
Variable (including weight factor) |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Sludge production cost index |  | – |  | 7938 | 16824.1562 |  |  |  | 12381.0781 | 6283.4613 | 8886.1562
Aeration energy cost index |  | – |  | 4000 | 4283.3778 |  |  |  | 4141.6889 | 200.3784 | 283.3778
Pumping energy cost index |  | – |  | 440.9 | 388.17 |  |  |  | 414.535 | 37.2857 | 52.73
Carbon source dosage cost index |  | – |  | 2400 | 0 |  |  |  | 1200 | 1697.0563 | 2400
Mixing energy cost index |  | – |  | 768 | 240 |  |  |  | 504 | 373.3524 | 528
Total Operational Cost Index (OCI) |  | – |  | 9208 | 21735.7039 |  |  |  | 15471.852 | 8858.4244 | 12527.7039
Effluent violations
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
95% percentile of effluent SNH (Ammonia95) |  | g N/m3 |  | 4.65 |  |  |  |  | 4.65 | #DIV/0! | 0
95% percentile of effluent total N (TN95) |  | g N/m3 |  | 15.1 |  |  |  |  | 15.1 | #DIV/0! | 0
95% percentile of effluent TSS (TSS95) |  | g COD/m3 |  | 20.1 |  |  |  |  | 20.1 | #DIV/0! | 0
Maximum effluent total N limit (18 mg N/l) was violated
during: |  | days |  | 0.37492 | 0.72917 |  |  |  | 0.55205 | 0.25049 | 0.35425
% of total evaluation time: |  | % |  | 0.103 | 10.42% |  |  |  | 0.10358 | 0.00082519 | 0.001167
number of violations: |  | – |  | 4 | 5 |  |  |  | 4.5 | 0.70711 | 1
Maximum effluent total COD limit (100 mg COD/l) was violated
during: |  | days |  | 0.21876 |  |  |  |  | 0.21876 | #DIV/0! | 0
% of total evaluation time: |  | % |  | 0.0601 |  |  |  |  | 0.0601 | #DIV/0! | 0
number of violations: |  | – |  | 3 |  |  |  |  | 3 | #DIV/0! | 0
Maximum effluent ammonia limit (4 mg N/l) was violated
during: |  | days |  | 30.1756 |  |  |  |  | 30.1756 | #DIV/0! | 0
% of total evaluation time: |  | % |  | 8.29 |  |  |  |  | 8.29 | #DIV/0! | 0
number of violations: |  | – |  | 172 |  |  |  |  | 172 | #DIV/0! | 0
Maximum effluent TSS limit (30 mg SS/l) was violated
during: |  | days |  | 1.4269 |  |  |  |  | 1.4269 | #DIV/0! | 0
% of total evaluation time: |  | % |  | 0.392 |  |  |  |  | 0.392 | #DIV/0! | 0
number of violations: |  | – |  | 12 |  |  |  |  | 12 | #DIV/0! | 0
Maximum effluent BOD5 limit (10 mg/l) was violated
during: |  | days |  | 0.4368 |  |  |  |  | 0.4368 | #DIV/0! | 0
% of total evaluation time: |  | % |  | 0.12 |  |  |  |  | 0.12 | #DIV/0! | 0
number of violations: |  | – |  | 5 |  |  |  |  | 5 | #DIV/0! | 0
N2O Emissions
-------------------
N2O emission during nitrification/denitrification (ANOX1) |  | kg N2O/d |  |  | 0.010872
N2O emission during nitrification/denitrification (ANOX1) |  | kg N2O/d |  |  | 0.011226
N2O emission during nitrification/denitrification (AER1) |  | kg N2O/d |  |  | 2.0247
N2O emission during nitrification/denitrification (AER2) |  | kg N2O/d |  |  | 1.2546
N2O emission during nitrification/denitrification (AER3) |  | kg N2O/d |  |  | 0.60701
N2O emission during nitrification/denitrification (total) |  | kg N2O/d |  |  | 3.9084

## Sheet2
Effluent average concentrations based on load
---------------------------------------------
Effluent average flow rate = 18061.3319 m3/d
Effluent average SI conc = 30 g COD/m3
Effluent average SS conc = 1.2287 g COD/m3
Effluent average XI conc = 4.7314 g COD/m3
Effluent average XS conc = 0.21347 g COD/m3
Effluent average XBH conc = 9.5411 g COD/m3
Effluent average XBA1 conc = 0.51303 g COD/m3
Effluent average XP conc = 1.8024 g COD/m3
Effluent average SO conc = 3.6474 g (-COD)/m3
Effluent average SNO3 conc = 14.3628 g N/m3
Effluent average SNH conc = 1.6635 g N/m3 (limit = 4 g N/m3)
Effluent average SND conc = 0.56392 g N/m3
Effluent average XND conc = 0.015767 g N/m3
Effluent average SALK conc = 3.8296 mol HCO3/m3
Effluent average TSS conc = 12.7131 g SS/m3 (limit = 30 g SS/m3)
Effluent average Temperature = 15 degC
Effluent average SNO2 conc = 0.10928 g N/m3
Effluent average SNO conc = 0.0049457 g N/m3
Effluent average SN2O conc = 0.002591 g N/m3
Effluent average SN2 conc = 13.3587 g N/m3
Effluent average XBA2 conc = 0.14944 g COD/m3
Effluent average Kjeldahl N conc = 3.5127 g N/m3
Effluent average total N conc = 17.9923 g N/m3 (limit = 18 g N/m3)
Effluent average total COD conc = 48.1796 g COD/m3 (limit = 100 g COD/m3)
Effluent average BOD5 conc = 3.1219 g/m3 (limit = 10 g/m3)
Effluent average load
---------------------
Effluent average SI load = 541.84 kg COD/day
Effluent average SS load = 22.1925 kg COD/day
Effluent average XI load = 85.455 kg COD/day
Effluent average XS load = 3.8555 kg COD/day
Effluent average XBH load = 172.3257 kg COD/day
Effluent average XBA1 load = 9.266 kg COD/day
Effluent average XP load = 32.5537 kg COD/day
Effluent average SO load = 65.8773 kg (-COD)/day
Effluent average SNO3 load = 259.412 kg N/day
Effluent average SNH load = 30.0442 kg N/day
Effluent average SND load = 10.1851 kg N/day
Effluent average XND load = 0.28477 kg N/day
Effluent average SALK load = 69.1685 kmol HCO3/day
Effluent average TSS load = 229.6162 kg SS/day
Effluent average SNO2 load = 1.9738 kg N/day
Effluent average SNO load = 0.089327 kg N/day
Effluent average SNO load = 0.046797 kg N/day
Effluent average SN2O load = 241.2758 kg N/day
Effluent average SN2 load = 2.6991 kg COD/day
Effluent average Kjeldahl N load = 63.4436 kg N/d
Effluent average total N load = 324.9656 kg N/d
Effluent average total COD load = 870.1875 kg COD/d
Effluent average BOD5 load = 48.8989 kg BOD5/d
Sludge for disposal average concentrations based on load
--------------------------------------------------------
Sludge for disposal average flow rate = 385 m3/d
Sludge for disposal average SI conc = 30 g COD/m3
Sludge for disposal average SS conc = 1.2028 g COD/m3
Sludge for disposal average XI conc = 2242.0409 g COD/m3
Sludge for disposal average XS conc = 99.3718 g COD/m3
Sludge for disposal average XBH conc = 4531.3677 g COD/m3
Sludge for disposal average XBA1 conc = 243.116 g COD/m3
Sludge for disposal average XP conc = 852.1393 g COD/m3
Sludge for disposal average SO conc = 3.8494 g (-COD)/m3
Sludge for disposal average SNO3 conc = 14.5001 g N/m3
Sludge for disposal average SNH conc = 1.4071 g N/m3
Sludge for disposal average SND conc = 0.55449 g N/m3
Sludge for disposal average XND conc = 7.3628 g N/m3
Sludge for disposal average SALK conc = 3.808 mol HCO3/m3
Sludge for disposal average TSS conc = 6029.3437 g SS/m3
Sludge for disposal average Temperature = 15 degC
Sludge for disposal average SNO2 conc = 0.085892 g N/m3
Sludge for disposal average SNO conc = 0.0040165 g N/m3
Sludge for disposal average SN2O conc = 0.0021152 g N/m3
Sludge for disposal average SN2 conc = 13.3549 g N/m3
Sludge for disposal average XBA2 conc = 71.0892 g COD/m3
Sludge for disposal average Kjeldahl N conc = 615.9598 g N/m3
Sludge for disposal average total N conc = 630.552 g N/m3
Sludge for disposal average total COD conc = 8070.3277 g COD/m3
Sludge for disposal average BOD5 conc = 1139.6254 g BOD5/m3
Sludge for disposal average load
--------------------------------
Sludge for disposal average SI load = 11.55 kg COD/day
Sludge for disposal average SS load = 0.46307 kg COD/day
Sludge for disposal average XI load = 863.1858 kg COD/day
Sludge for disposal average XS load = 38.2581 kg COD/day
Sludge for disposal average XBH load = 1744.5766 kg COD/day
Sludge for disposal average XBA load = 93.5996 kg COD/day
Sludge for disposal average XP load = 328.0736 kg COD/day
Sludge for disposal average SO load = 1.482 kg (-COD)/day
Sludge for disposal average SNO3 load = 5.5826 kg N/day
Sludge for disposal average SNH load = 0.54173 kg N/day
Sludge for disposal average SND load = 0.21348 kg N/day
Sludge for disposal average XND load = 2.8347 kg N/day
Sludge for disposal average SALK load = 1.4661 kmol HCO3/day
Sludge for disposal average TSS load = 2321.2973 kg SS/day
Sludge for disposal average SNO2 load = 0.033068 kg N/day
Sludge for disposal average SNO load = 0.0015463 kg N/day
Sludge for disposal average SN2O load = 0.00081437 kg N/day
Sludge for disposal average SN2 load = 5.1416 kg N/day
Sludge for disposal average XBA2 load = 27.3693 kg N/day
Sludge for disposal average Kjeldahl N load = 235.5024 kg N/d
Sludge for disposal average total N load = 241.1203 kg N/d
Sludge for disposal average total COD load = 3107.0762 kg COD/d
Sludge for disposal average BOD5 load = 438.7558 kg BOD5/d
Other effluent quality variables
--------------------------------
Influent Quality Index (IQI) = 52174.9257 kg poll.units/d
Effluent Quality Index (EQI) = 5953.7576 kg poll.units/d
Sludge production for disposal = 39256.3644 kg SS
Average sludge production for disposal per day = 5608.0521 kg SS/d
Sludge production released into effluent = 1607.3137 kg SS
Average sludge production released into effluent per day = 229.6162 kg SS/d
Total sludge production = 40863.678 kg SS
Total average sludge production per day = 5837.6683 kg SS/d
Average aeration energy = 4283.3778 kWh/d
Average pumping energy = 388.17 kWh/d
Average carbon source addition = 0 kg COD/d
Average mixing energy = 240 kWh/d
Operational Cost Index
----------------------
Sludge production cost index = 16824.1562
Aeration energy cost index = 4283.3778
Pumping energy cost index = 388.17
Carbon source dosage cost index = 0
Mixing energy cost index = 240
Total Operational Cost Index (OCI) = 21735.7039
N2O Emissions
-------------------
N2O emission during nitrification/denitrification (ANOX1) = 0.010872 kg N2O/d
N2O emission during nitrification/denitrification (ANOX1) = 0.011226 kg N2O/d
N2O emission during nitrification/denitrification (AER1) = 2.0247 kg N2O/d
N2O emission during nitrification/denitrification (AER2) = 1.2546 kg N2O/d
N2O emission during nitrification/denitrification (AER3) = 0.60701 kg N2O/d
N2O emission during nitrification/denitrification (total) = 3.9084 kg N2O/d
Effluent violations
-------------------
The maximum effluent ammonia nitrogen level (4 g N/m3) was violated
during 0.72917 days, i.e. 10.4167% of the operating time.
The limit was violated at 5 different occasions.
***** Plant evaluation of BSM2 system successfully finished *****
End time (hour:min:sec) = 16 13 12