## BSM2 OL (1 year)
Ring test BSM 1G |  | Openloop
Model component tested: | COMPLETE BSM1G | STATUS: | Integrated system | Dynamic | Openloop
See detailed specifications at the end of this sheet!
Test of BSM1G for full dynamics in openloop based on the finalised BSM2 and finalised evaluation criteria
Simulation procedure: simulate to steady state using CONSTANT INFLUENT and use final state variable values for initial values for dynamic simulation.
Run full 14 days simulation using input file from BSM web site and base evaluation on the last 7 days, i.e. from beginning of day 7.
Evaluation is based on data every 15 minutes and uses zero-order hold (forward Euler) for integration between measurements.
PLANT EVALUATION 1 YEAR (364 DAYS)
Effluent average concentrations based on load, including bypass
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Effluent average flow rate |  | m3/d |  |  | 18061.1402 |  | 18062.0362 |  | 18061.5882 | 0.63359 | 0.89603
Effluent average SI concentration |  | g COD/m3 |  |  | 30 |  | 30 |  | 30 | 0 | 0
Effluent average SS concentration |  | g COD/m3 |  |  | 1.2306 |  | 1.2277 |  | 1.2291 | 0.0020632 | 0.0029178
Effluent average XI concentration |  | g COD/m3 |  |  | 4.6965 |  | 4.6848 |  | 4.6906 | 0.0083021 | 0.011741
Effluent average XS concentration |  | g COD/m3 |  |  | 0.22233 |  | 0.2214 |  | 0.22186 | 0.00065786 | 0.00093035
Effluent average XBH concentration |  | g COD/m3 |  |  | 9.8359 |  | 9.8217 |  | 9.8288 | 0.010054 | 0.014218
Effluent average XBA1 concentration |  | g COD/m3 |  |  | 0.51375 |  | 0.51306 |  | 0.5134 | 0.00048978 | 0.00069265
Effluent average XP concentration |  | g COD/m3 |  |  | 1.6913 |  | 1.6896 |  | 1.6904 | 0.0012102 | 0.0017115
Effluent average SO concentration |  | g -COD/m3 |  |  | 3.5121 |  | 3.5275 |  | 3.5198 | 0.010859 | 0.015356
Effluent average SNO3 concentration |  | g N/m3 |  |  | 14.677 |  | 14.686 |  | 14.6815 | 0.0063653 | 0.0090019 | 0.026475
Effluent average SNH concentration (limit = 4 g N/m3) |  | g N/m3 |  |  | 1.955 |  | 1.9278 |  | 1.9414 | 0.019236 | 0.027204 | 0.20534
Effluent average SND concentration |  | g N/m3 |  |  | 0.56023 |  | 0.5592 |  | 0.55972 | 0.00072553 | 0.0010261
Effluent average XND concentration |  | g N/m3 |  |  | 0.016419 |  | 0.016357 |  | 0.016388 | 4.4058e-05 | 6.2307e-05
Effluent average SALK concentration |  | mol HCO3-/m3 |  |  | 3.8312 |  | 3.8329 |  | 3.832 | 0.0011902 | 0.0016832
Effluent average TSS concentration (limit = 30 g SS/m3) |  | g/m3 |  |  | 12.8533 |  | 12.8312 |  | 12.8422 | 0.015632 | 0.022107
Effluent average Temperature |  | deg C |  |  | 15 |  | 15 |  | 15 | 0 | 0
Effluent average SNO2 conc |  | g N/m3 |  |  | 0.033459 |  | 0.032767 |  | 0.033113 | 0.00048936 | 0.00069205
Effluent average SNO conc |  | g N/m3 |  |  | 0.0021944 |  | 0.0021547 |  | 0.0021746 | 2.805e-05 | 3.9669e-05
Effluent average SN2O conc |  | g N/m3 |  |  | 0.0011647 |  | 0.0011433 |  | 0.001154 | 1.5125e-05 | 2.139e-05
Effluent average SN2 conc |  | g N/m3 |  |  | 13.3919 |  | 13.3915 |  | 13.3917 | 0.00031722 | 0.00044862
Effluent average XBA2 conc |  | g COD/m3 |  |  | 0.17795 |  | 0.17777 |  | 0.17786 | 0.0001264 | 0.00017876
Effluent average Kjeldahl N conc |  | g N/m3 |  |  | 3.8203 |  | 3.7899 |  | 3.8051 | 0.021501
Effluent average total N concentration (limit = 18 g N/l) |  | g N/m3 |  |  | 18.5341 |  | 18.512 |  | 18.523 | 0.015655 | 0.02214
Effluent average total COD concentration (limit = 100 g COD/m3) |  | g COD/m3 |  |  | 48.3684 |  | 48.3359 |  | 48.3522 | 0.022953 | 0.03246
Effluent average BOD5 concentration (limit = 10 g/m3) |  | g/m3 |  |  | 2.7846 |  | 2.7801 |  | 2.7824 | 0.0031482 | 0.0044522
Effluent average load, including bypass
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Effluent average SI load |  | kg COD/day |  |  | 541.8342 |  | 541.8633 |  | 541.8488 | 0.020597 | 0.029128
Effluent average SS load |  | kg COD/day |  |  | 22.2265 |  | 22.1738 |  | 22.2001 | 0.037299 | 0.052749
Effluent average XI load |  | kg COD/day |  |  | 84.8246 |  | 84.6157 |  | 84.7202 | 0.14769 | 0.20887
Effluent average XS load |  | kg COD/day |  |  | 4.0155 |  | 3.9988 |  | 4.0071 | 0.011838 | 0.016742
Effluent average XBH load |  | kg COD/day |  |  | 177.6476 |  | 177.3984 |  | 177.523 | 0.17623 | 0.24923
Effluent average XBA1 load |  | kg COD/day |  |  | 9.2788 |  | 9.2668 |  | 9.2728 | 0.0084746 | 0.011985
Effluent average XP load |  | kg COD/day |  |  | 30.5469 |  | 30.5173 |  | 30.5321 | 0.020927 | 0.029596
Effluent average SO load |  | kg -COD/day |  |  | 63.4318 |  | 63.7174 |  | 63.5746 | 0.20197 | 0.28563
Effluent average SNO3 load |  | kg N/day |  |  | 265.0828 |  | 265.2618 |  | 265.1723 | 0.12656 | 0.17898
Effluent average SNH load |  | kg N/day |  |  | 35.3097 |  | 34.8162 |  | 35.0629 | 0.34897 | 0.49352
Effluent average SND load |  | kg N/day |  |  | 10.1184 |  | 10.1002 |  | 10.1093 | 0.012903 | 0.018248
Effluent average XND load |  | kg N/day |  |  | 0.29655 |  | 0.29542 |  | 0.29599 | 0.00079587 | 0.0011255
Effluent average SALK load |  | kmol HCO3-/day |  |  | 69.1962 |  | 69.2301 |  | 69.2131 | 0.023936 | 0.03385
Effluent average TSS load |  | kg/day |  |  | 232.1456 |  | 231.7559 |  | 231.9508 | 0.27555 | 0.38969
Effluent average SNO2 load |  | kg N/day |  |  | 0.60431 |  | 0.59178 |  | 0.59804 | 0.0088621 | 0.012533
Effluent average SNO load |  | kg N/day |  |  | 0.039634 |  | 0.038915 |  | 0.039274 | 0.00050845 | 0.00071906
Effluent average SN2O load |  | kg N/day |  |  | 0.021037 |  | 0.020648 |  | 0.020843 | 0.00027475 | 0.00038856
Effluent average SN2 load |  | kg N/day |  |  | 241.8735 |  | 241.8778 |  | 241.8756 | 0.0030394 | 0.0042984
Effluent average XBA2 load |  | kg COD/day |  |  | 3.2141 |  | 3.2109 |  | 3.2125 | 0.0022661 | 0.0032048
Effluent average Kjeldahl N load |  | kg N/day |  |  | 68.999 |  | 68.4491 |  | 68.724 | 0.38885 | 0.54991
Effluent average total N load |  | kg N/day |  |  | 334.7469 |  | 334.3622 |  | 334.5546 | 0.27202 | 0.3847
Effluent average total COD load |  | kg COD/day |  |  | 873.5881 |  | 873.045 |  | 873.3165 | 0.38406 | 0.54314
Effluent average BOD5 load |  | kg/day |  |  | 50.2928 |  | 50.2146 |  | 50.2537 | 0.055277 | 0.078173
Other output quality variables
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Influent quality (I.Q.) index |  | kg poll.units/day |  |  | 52174.9256 |  | 52177.2907 |  | 52176.1082 | 1.6724 | 2.3651
Effluent quality (E.Q.) index |  | kg poll.units/day |  |  | 6179.9655 |  | 6149.6914 |  | 6164.8285 | 21.407 | 30.2741
Average sludge production for disposal per day |  | kg SS/day |  |  | 2352.0419 |  | 2350.2708 |  | 2351.1564 | 1.2523 | 1.7711
Average sludge production released into effluent per day |  | kg SS/day |  |  | 232.1456 |  | 231.7575 |  | 231.9515 | 0.27445 | 0.38813
Total average sludge production per day |  | kg SS/day |  |  | 2584.1875 |  | 2582.0283 |  | 2583.1079 | 1.5268 | 2.1592
'Energy' related variables
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Average aeration energy |  | kWh/d |  |  | 4283.3778 |  | 4283.3778 |  | 4283.3778 | 1.5713e-05 | 2.2222e-05
Average pumping energy |  | kWh/d |  |  | 388.17 |  | 388.17 |  | 388.17 | 0 | 0
Average carbon source dosage |  | kg COD/day |  |  | 0 |  | 0 |  | 0 | 0 | 0
Average mixing energy |  | kWh/d |  |  | 240 |  | 240.4565 |  | 240.2283 | 0.3228 | 0.45651
Operational cost index
Variable (including weight factor) |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
Sludge production cost index |  | – |  |  | 11760.2094 |  | 11751.3542 |  | 11755.7818 | 6.2616 | 8.8552
Aeration energy cost index |  | – |  |  | 4283.3778 |  | 4283.3778 |  | 4283.3778 | 1.5713e-05 | 2.2222e-05
Pumping energy cost index |  | – |  |  | 388.17 |  | 388.17 |  | 388.17 | 0 | 0
Carbon source dosage cost index |  | – |  |  | 0 |  | 0 |  | 0 | 0 | 0
Mixing energy cost index |  | – |  |  | 240 |  | 240.4565 |  | 240.2283 | 0.3228 | 0.45651
Total Operational Cost Index (OCI) |  | – |  |  | 16671.7572 |  | 16663.3585 |  | 16667.5578 | 5.9388 | 8.3987
Effluent violations
Variable |  | Unit | GPS-X | FORTRAN | MATLAB | SIMBA | WEST | STOAT | AVERAGE | STANDARD DEV | RANGE (MAX-MIN)
95% percentile of effluent SNH (Ammonia95) |  | g N/m3 |  |  | 6.8302 |  | 6.7934 |  | 6.8118 | 0.026012 | 0.036786
95% percentile of effluent total N (TN95) |  | g N/m3 |  |  | 22.7697 |  | 22.7073 |  | 22.7385 | 0.044134 | 0.062415
95% percentile of effluent TSS (TSS95) |  | g COD/m3 |  |  | 15.5764 |  | 15.5522 |  | 15.5643 | 0.017118 | 0.024209
Maximum effluent total N limit (18 mg N/l) was violated
during: |  | days |  |  | 3.0625 |  | 1.5105 |  | 2.2865 | 1.0974 | 1.552
% of total evaluation time: |  | % |  |  | 43.75% |  | 21.5786 |  | 11.0081 | 14.949 | 21.1411
number of violations: |  | – |  |  | 7 |  | 6 |  | 6.5 | 0.70711 | 1
Maximum effluent total COD limit (100 mg COD/l) was violated
during: |  | days | [6 empty] | #DIV/0! | #DIV/0! | 0
% of total evaluation time: |  | % | [6 empty] | #DIV/0! | #DIV/0! | 0
number of violations: |  | – | [6 empty] | #DIV/0! | #DIV/0! | 0
Maximum effluent ammonia limit (4 mg N/l) was violated
during: |  | days |  |  | 0.83333 |  | 0.81253 |  | 0.82293 | 0.01471 | 0.020803
% of total evaluation time: |  | % |  |  | 11.9048 |  | 11.6076 |  | 11.7562 | 0.21014 | 0.29718
number of violations: |  | – |  |  | 5 |  | 5 |  | 5 | 0 | 0
Maximum effluent TSS limit (30 mg SS/l) was violated
during: |  | days | [6 empty] | #DIV/0! | #DIV/0! | 0
% of total evaluation time: |  | % | [6 empty] | #DIV/0! | #DIV/0! | 0
number of violations: |  | – | [6 empty] | #DIV/0! | #DIV/0! | 0
Maximum effluent BOD5 limit (10 mg/l) was violated
during: |  | days | [6 empty] | #DIV/0! | #DIV/0! | 0
% of total evaluation time: |  | % | [6 empty] | #DIV/0! | #DIV/0! | 0
number of violations: |  | – | [6 empty] | #DIV/0! | #DIV/0! | 0
N2O Emissions
-------------------
N2O emission during nitrification/denitrification (ANOX1) |  | kg N2O/d |  |  | 0.016405 |  | 0.016408 |  | 0.016406 | 1.9337e-06 | 2.7347e-06
N2O emission during nitrification/denitrification (ANOX1) |  | kg N2O/d |  |  | 0.017492 |  | 0.017495 |  | 0.017494 | 2.3192e-06 | 3.2799e-06
N2O emission during nitrification/denitrification (AER1) |  | kg N2O/d |  |  | 1.9147 |  | 1.9103 |  | 1.9125 | 0.0031094 | 0.0043973
N2O emission during nitrification/denitrification (AER2) |  | kg N2O/d |  |  | 0.95557 |  | 0.95093 |  | 0.95325 | 0.0032794 | 0.0046377
N2O emission during nitrification/denitrification (AER3) |  | kg N2O/d |  |  | 0.43506 |  | 0.4314 |  | 0.43323 | 0.0025856 | 0.0036566
N2O emission during nitrification/denitrification (total) |  | kg N2O/d |  |  | 3.3393 |  | 3.3265 |  | 3.3329 | 0.0090217 | 0.012759
b

## Sheet2
Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load | Effluent average concentrations based on load
--------------------------------------------- | --------------------------------------------- | --------------------------------------------- | ---------------------------------------------
Effluent average flow rate = 18061.1402 m3/d | Effluent average flow rate = 18061.1402 m3/d | Effluent average flow rate = 18061.1455 m3/d | Effluent average flow rate = 18061.1455 m3/d
Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3 | Effluent average SI conc = 30 g COD/m3
Effluent average SS conc = 1.2306 g COD/m3 | Effluent average SS conc = 1.2306 g COD/m3 | Effluent average SS conc = 1.2306 g COD/m3 | Effluent average SS conc = 1.2306 g COD/m3
Effluent average XI conc = 4.6965 g COD/m3 | Effluent average XI conc = 4.6965 g COD/m3 | Effluent average XI conc = 4.6965 g COD/m3 | Effluent average XI conc = 4.6965 g COD/m3
Effluent average XS conc = 0.22233 g COD/m3 | Effluent average XS conc = 0.22233 g COD/m3 | Effluent average XS conc = 0.22233 g COD/m3 | Effluent average XS conc = 0.22233 g COD/m3
Effluent average XBH conc = 9.8359 g COD/m3 | Effluent average XBH conc = 9.8359 g COD/m3 | Effluent average XBH conc = 9.8359 g COD/m3 | Effluent average XBH conc = 9.8359 g COD/m3
Effluent average XBA1 conc = 0.51375 g COD/m3 | Effluent average XBA1 conc = 0.51375 g COD/m3 | Effluent average XBA1 conc = 0.51375 g COD/m3 | Effluent average XBA1 conc = 0.51375 g COD/m3
Effluent average XP conc = 1.6913 g COD/m3 | Effluent average XP conc = 1.6913 g COD/m3 | Effluent average XP conc = 1.6913 g COD/m3 | Effluent average XP conc = 1.6913 g COD/m3
Effluent average SO conc = 3.5121 g (-COD)/m3 | Effluent average SO conc = 3.5121 g (-COD)/m3 | Effluent average SO conc = 3.5121 g (-COD)/m3 | Effluent average SO conc = 3.5121 g (-COD)/m3
Effluent average SNO3 conc = 14.677 g N/m3 | Effluent average SNO3 conc = 14.677 g N/m3 | Effluent average SNO3 conc = 14.677 g N/m3 | Effluent average SNO3 conc = 14.677 g N/m3
Effluent average SNH conc = 1.955 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.955 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.955 g N/m3 (limit = 4 g N/m3) | Effluent average SNH conc = 1.955 g N/m3 (limit = 4 g N/m3)
Effluent average SND conc = 0.56023 g N/m3 | Effluent average SND conc = 0.56023 g N/m3 | Effluent average SND conc = 0.56023 g N/m3 | Effluent average SND conc = 0.56023 g N/m3
Effluent average XND conc = 0.016419 g N/m3 | Effluent average XND conc = 0.016419 g N/m3 | Effluent average XND conc = 0.016419 g N/m3 | Effluent average XND conc = 0.016419 g N/m3
Effluent average SALK conc = 3.8312 mol HCO3/m3 | Effluent average SALK conc = 3.8312 mol HCO3/m3 | Effluent average SALK conc = 3.8312 mol HCO3/m3 | Effluent average SALK conc = 3.8312 mol HCO3/m3
Effluent average TSS conc = 12.8533 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8533 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8533 g SS/m3 (limit = 30 g SS/m3) | Effluent average TSS conc = 12.8533 g SS/m3 (limit = 30 g SS/m3)
Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC | Effluent average Temperature = 15 degC
Effluent average SNO2 conc = 0.033459 g N/m3 | Effluent average SNO2 conc = 0.033459 g N/m3 | Effluent average SNO2 conc = 0.033459 g N/m3 | Effluent average SNO2 conc = 0.033459 g N/m3
Effluent average SNO conc = 0.0021944 g N/m3 | Effluent average SNO conc = 0.0021944 g N/m3 | Effluent average SNO conc = 0.0021944 g N/m3 | Effluent average SNO conc = 0.0021944 g N/m3
Effluent average SN2O conc = 0.0011647 g N/m3 | Effluent average SN2O conc = 0.0011647 g N/m3 | Effluent average SN2O conc = 0.0011647 g N/m3 | Effluent average SN2O conc = 0.0011647 g N/m3
Effluent average SN2 conc = 13.3919 g N/m3 | Effluent average SN2 conc = 13.3919 g N/m3 | Effluent average SN2 conc = 13.3919 g N/m3 | Effluent average SN2 conc = 13.3919 g N/m3
Effluent average XBA2 conc = 0.17795 g COD/m3 | Effluent average XBA2 conc = 0.17795 g COD/m3 | Effluent average XBA2 conc = 0.17795 g COD/m3 | Effluent average XBA2 conc = 0.17795 g COD/m3
Effluent average Kjeldahl N conc = 3.8203 g N/m3 | Effluent average Kjeldahl N conc = 3.8203 g N/m3 | Effluent average Kjeldahl N conc = 3.8203 g N/m3 | Effluent average Kjeldahl N conc = 3.8203 g N/m3
Effluent average total N conc = 18.5341 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 18.5341 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 18.5341 g N/m3 (limit = 18 g N/m3) | Effluent average total N conc = 18.5341 g N/m3 (limit = 18 g N/m3)
Effluent average total COD conc = 48.3684 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3684 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3684 g COD/m3 (limit = 100 g COD/m3) | Effluent average total COD conc = 48.3684 g COD/m3 (limit = 100 g COD/m3)
Effluent average BOD5 conc = 2.7846 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 2.7846 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 2.7846 g/m3 (limit = 10 g/m3) | Effluent average BOD5 conc = 2.7846 g/m3 (limit = 10 g/m3)
Effluent average load | Effluent average load | Effluent average load | Effluent average load
--------------------- | --------------------- | --------------------- | ---------------------
Effluent average SI load = 541.8342 kg COD/day | Effluent average SI load = 541.8342 kg COD/day | Effluent average SI load = 541.8344 kg COD/day | Effluent average SI load = 541.8344 kg COD/day
Effluent average SS load = 22.2265 kg COD/day | Effluent average SS load = 22.2265 kg COD/day | Effluent average SS load = 22.2265 kg COD/day | Effluent average SS load = 22.2265 kg COD/day
Effluent average XI load = 84.8246 kg COD/day | Effluent average XI load = 84.8246 kg COD/day | Effluent average XI load = 84.8246 kg COD/day | Effluent average XI load = 84.8246 kg COD/day
Effluent average XS load = 4.0155 kg COD/day | Effluent average XS load = 4.0155 kg COD/day | Effluent average XS load = 4.0155 kg COD/day | Effluent average XS load = 4.0155 kg COD/day
Effluent average XBH load = 177.6476 kg COD/day | Effluent average XBH load = 177.6476 kg COD/day | Effluent average XBH load = 177.6477 kg COD/day | Effluent average XBH load = 177.6477 kg COD/day
Effluent average XBA1 load = 9.2788 kg COD/day | Effluent average XBA1 load = 9.2788 kg COD/day | Effluent average XBA1 load = 9.2788 kg COD/day | Effluent average XBA1 load = 9.2788 kg COD/day
Effluent average XP load = 30.5469 kg COD/day | Effluent average XP load = 30.5469 kg COD/day | Effluent average XP load = 30.5469 kg COD/day | Effluent average XP load = 30.5469 kg COD/day
Effluent average SO load = 63.4318 kg (-COD)/day | Effluent average SO load = 63.4318 kg (-COD)/day | Effluent average SO load = 63.4318 kg (-COD)/day | Effluent average SO load = 63.4318 kg (-COD)/day
Effluent average SNO3 load = 265.0828 kg N/day | Effluent average SNO3 load = 265.0828 kg N/day | Effluent average SNO3 load = 265.083 kg N/day | Effluent average SNO3 load = 265.083 kg N/day
Effluent average SNH load = 35.3097 kg N/day | Effluent average SNH load = 35.3097 kg N/day | Effluent average SNH load = 35.3097 kg N/day | Effluent average SNH load = 35.3097 kg N/day
Effluent average SND load = 10.1184 kg N/day | Effluent average SND load = 10.1184 kg N/day | Effluent average SND load = 10.1184 kg N/day | Effluent average SND load = 10.1184 kg N/day
Effluent average XND load = 0.29655 kg N/day | Effluent average XND load = 0.29655 kg N/day | Effluent average XND load = 0.29655 kg N/day | Effluent average XND load = 0.29655 kg N/day
Effluent average SALK load = 69.1962 kmol HCO3/day | Effluent average SALK load = 69.1962 kmol HCO3/day | Effluent average SALK load = 69.1962 kmol HCO3/day | Effluent average SALK load = 69.1962 kmol HCO3/day
Effluent average TSS load = 232.1456 kg SS/day | Effluent average TSS load = 232.1456 kg SS/day | Effluent average TSS load = 232.1456 kg SS/day | Effluent average TSS load = 232.1456 kg SS/day
Effluent average SNO2 load = 0.60431 kg N/day | Effluent average SNO2 load = 0.60431 kg N/day | Effluent average SNO2 load = 0.60431 kg N/day | Effluent average SNO2 load = 0.60431 kg N/day
Effluent average SNO load = 0.039634 kg N/day | Effluent average SNO load = 0.039634 kg N/day | Effluent average SNO load = 0.039634 kg N/day | Effluent average SNO load = 0.039634 kg N/day
Effluent average SNO load = 0.021037 kg N/day | Effluent average SNO load = 0.021037 kg N/day | Effluent average SNO load = 0.021037 kg N/day | Effluent average SNO load = 0.021037 kg N/day
Effluent average SN2O load = 241.8735 kg N/day | Effluent average SN2O load = 241.8735 kg N/day | Effluent average SN2O load = 241.8736 kg N/day | Effluent average SN2O load = 241.8736 kg N/day
Effluent average SN2 load = 3.2141 kg COD/day | Effluent average SN2 load = 3.2141 kg COD/day | Effluent average SN2 load = 3.2141 kg COD/day | Effluent average SN2 load = 3.2141 kg COD/day
Effluent average Kjeldahl N load = 68.999 kg N/d | Effluent average Kjeldahl N load = 68.999 kg N/d | Effluent average Kjeldahl N load = 68.999 kg N/d | Effluent average Kjeldahl N load = 68.999 kg N/d
Effluent average total N load = 334.7469 kg N/d | Effluent average total N load = 334.7469 kg N/d | Effluent average total N load = 334.747 kg N/d | Effluent average total N load = 334.747 kg N/d
Effluent average total COD load = 873.5881 kg COD/d | Effluent average total COD load = 873.5881 kg COD/d | Effluent average total COD load = 873.5883 kg COD/d | Effluent average total COD load = 873.5883 kg COD/d
Effluent average BOD5 load = 50.2928 kg BOD5/d | Effluent average BOD5 load = 50.2928 kg BOD5/d | Effluent average BOD5 load = 50.2928 kg BOD5/d | Effluent average BOD5 load = 50.2928 kg BOD5/d
Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load | Sludge for disposal average concentrations based on load
-------------------------------------------------------- | -------------------------------------------------------- | -------------------------------------------------------- | --------------------------------------------------------
Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d | Sludge for disposal average flow rate = 385 m3/d
Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3 | Sludge for disposal average SI conc = 30 g COD/m3
Sludge for disposal average SS conc = 1.1912 g COD/m3 | Sludge for disposal average SS conc = 1.1912 g COD/m3 | Sludge for disposal average SS conc = 1.1912 g COD/m3 | Sludge for disposal average SS conc = 1.1912 g COD/m3
Sludge for disposal average XI conc = 2250.6252 g COD/m3 | Sludge for disposal average XI conc = 2250.6252 g COD/m3 | Sludge for disposal average XI conc = 2250.6252 g COD/m3 | Sludge for disposal average XI conc = 2250.6252 g COD/m3
Sludge for disposal average XS conc = 103.0049 g COD/m3 | Sludge for disposal average XS conc = 103.0049 g COD/m3 | Sludge for disposal average XS conc = 103.0049 g COD/m3 | Sludge for disposal average XS conc = 103.0049 g COD/m3
Sludge for disposal average XBH conc = 4718.4629 g COD/m3 | Sludge for disposal average XBH conc = 4718.4629 g COD/m3 | Sludge for disposal average XBH conc = 4718.4629 g COD/m3 | Sludge for disposal average XBH conc = 4718.4629 g COD/m3
Sludge for disposal average XBA1 conc = 246.1209 g COD/m3 | Sludge for disposal average XBA1 conc = 246.1209 g COD/m3 | Sludge for disposal average XBA1 conc = 246.1209 g COD/m3 | Sludge for disposal average XBA1 conc = 246.1209 g COD/m3
Sludge for disposal average XP conc = 809.9242 g COD/m3 | Sludge for disposal average XP conc = 809.9242 g COD/m3 | Sludge for disposal average XP conc = 809.9242 g COD/m3 | Sludge for disposal average XP conc = 809.9242 g COD/m3
Sludge for disposal average SO conc = 3.7797 g (-COD)/m3 | Sludge for disposal average SO conc = 3.7797 g (-COD)/m3 | Sludge for disposal average SO conc = 3.7797 g (-COD)/m3 | Sludge for disposal average SO conc = 3.7797 g (-COD)/m3
Sludge for disposal average SNO3 conc = 14.8548 g N/m3 | Sludge for disposal average SNO3 conc = 14.8548 g N/m3 | Sludge for disposal average SNO3 conc = 14.8548 g N/m3 | Sludge for disposal average SNO3 conc = 14.8548 g N/m3
Sludge for disposal average SNH conc = 1.6044 g N/m3 | Sludge for disposal average SNH conc = 1.6044 g N/m3 | Sludge for disposal average SNH conc = 1.6044 g N/m3 | Sludge for disposal average SNH conc = 1.6044 g N/m3
Sludge for disposal average SND conc = 0.54703 g N/m3 | Sludge for disposal average SND conc = 0.54703 g N/m3 | Sludge for disposal average SND conc = 0.54703 g N/m3 | Sludge for disposal average SND conc = 0.54703 g N/m3
Sludge for disposal average XND conc = 7.6497 g N/m3 | Sludge for disposal average XND conc = 7.6497 g N/m3 | Sludge for disposal average XND conc = 7.6497 g N/m3 | Sludge for disposal average XND conc = 7.6497 g N/m3
Sludge for disposal average SALK conc = 3.8005 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8005 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8005 mol HCO3/m3 | Sludge for disposal average SALK conc = 3.8005 mol HCO3/m3
Sludge for disposal average TSS conc = 6160.039 g SS/m3 | Sludge for disposal average TSS conc = 6160.039 g SS/m3 | Sludge for disposal average TSS conc = 6160.039 g SS/m3 | Sludge for disposal average TSS conc = 6160.039 g SS/m3
Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC | Sludge for disposal average Temperature = 15 degC
Sludge for disposal average SNO2 conc = 0.026809 g N/m3 | Sludge for disposal average SNO2 conc = 0.026809 g N/m3 | Sludge for disposal average SNO2 conc = 0.026809 g N/m3 | Sludge for disposal average SNO2 conc = 0.026809 g N/m3
Sludge for disposal average SNO conc = 0.0017844 g N/m3 | Sludge for disposal average SNO conc = 0.0017844 g N/m3 | Sludge for disposal average SNO conc = 0.0017844 g N/m3 | Sludge for disposal average SNO conc = 0.0017844 g N/m3
Sludge for disposal average SN2O conc = 0.0009471 g N/m3 | Sludge for disposal average SN2O conc = 0.0009471 g N/m3 | Sludge for disposal average SN2O conc = 0.0009471 g N/m3 | Sludge for disposal average SN2O conc = 0.0009471 g N/m3
Sludge for disposal average SN2 conc = 13.3847 g N/m3 | Sludge for disposal average SN2 conc = 13.3847 g N/m3 | Sludge for disposal average SN2 conc = 13.3847 g N/m3 | Sludge for disposal average SN2 conc = 13.3847 g N/m3
Sludge for disposal average XBA2 conc = 85.2472 g COD/m3 | Sludge for disposal average XBA2 conc = 85.2472 g COD/m3 | Sludge for disposal average XBA2 conc = 85.2472 g COD/m3 | Sludge for disposal average XBA2 conc = 85.2472 g COD/m3
Sludge for disposal average Kjeldahl N conc = 632.8344 g N/m3 | Sludge for disposal average Kjeldahl N conc = 632.8344 g N/m3 | Sludge for disposal average Kjeldahl N conc = 632.8344 g N/m3 | Sludge for disposal average Kjeldahl N conc = 632.8344 g N/m3
Sludge for disposal average total N conc = 647.7188 g N/m3 | Sludge for disposal average total N conc = 647.7188 g N/m3 | Sludge for disposal average total N conc = 647.7188 g N/m3 | Sludge for disposal average total N conc = 647.7188 g N/m3
Sludge for disposal average total COD conc = 8244.5765 g COD/m3 | Sludge for disposal average total COD conc = 8244.5765 g COD/m3 | Sludge for disposal average total COD conc = 8244.5765 g COD/m3 | Sludge for disposal average total COD conc = 8244.5765 g COD/m3
Sludge for disposal average BOD5 conc = 1187.5102 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1187.5102 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1187.5102 g BOD5/m3 | Sludge for disposal average BOD5 conc = 1187.5102 g BOD5/m3
Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load | Sludge for disposal average load
-------------------------------- | -------------------------------- | -------------------------------- | --------------------------------
Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day | Sludge for disposal average SI load = 11.55 kg COD/day
Sludge for disposal average SS load = 0.45862 kg COD/day | Sludge for disposal average SS load = 0.45862 kg COD/day | Sludge for disposal average SS load = 0.45862 kg COD/day | Sludge for disposal average SS load = 0.45862 kg COD/day
Sludge for disposal average XI load = 866.4907 kg COD/day | Sludge for disposal average XI load = 866.4907 kg COD/day | Sludge for disposal average XI load = 866.4907 kg COD/day | Sludge for disposal average XI load = 866.4907 kg COD/day
Sludge for disposal average XS load = 39.6569 kg COD/day | Sludge for disposal average XS load = 39.6569 kg COD/day | Sludge for disposal average XS load = 39.6569 kg COD/day | Sludge for disposal average XS load = 39.6569 kg COD/day
Sludge for disposal average XBH load = 1816.6082 kg COD/day | Sludge for disposal average XBH load = 1816.6082 kg COD/day | Sludge for disposal average XBH load = 1816.6082 kg COD/day | Sludge for disposal average XBH load = 1816.6082 kg COD/day
Sludge for disposal average XBA load = 94.7566 kg COD/day | Sludge for disposal average XBA load = 94.7566 kg COD/day | Sludge for disposal average XBA load = 94.7566 kg COD/day | Sludge for disposal average XBA load = 94.7566 kg COD/day
Sludge for disposal average XP load = 311.8208 kg COD/day | Sludge for disposal average XP load = 311.8208 kg COD/day | Sludge for disposal average XP load = 311.8208 kg COD/day | Sludge for disposal average XP load = 311.8208 kg COD/day
Sludge for disposal average SO load = 1.4552 kg (-COD)/day | Sludge for disposal average SO load = 1.4552 kg (-COD)/day | Sludge for disposal average SO load = 1.4552 kg (-COD)/day | Sludge for disposal average SO load = 1.4552 kg (-COD)/day
Sludge for disposal average SNO3 load = 5.7191 kg N/day | Sludge for disposal average SNO3 load = 5.7191 kg N/day | Sludge for disposal average SNO3 load = 5.7191 kg N/day | Sludge for disposal average SNO3 load = 5.7191 kg N/day
Sludge for disposal average SNH load = 0.61771 kg N/day | Sludge for disposal average SNH load = 0.61771 kg N/day | Sludge for disposal average SNH load = 0.61771 kg N/day | Sludge for disposal average SNH load = 0.61771 kg N/day
Sludge for disposal average SND load = 0.21061 kg N/day | Sludge for disposal average SND load = 0.21061 kg N/day | Sludge for disposal average SND load = 0.21061 kg N/day | Sludge for disposal average SND load = 0.21061 kg N/day
Sludge for disposal average XND load = 2.9451 kg N/day | Sludge for disposal average XND load = 2.9451 kg N/day | Sludge for disposal average XND load = 2.9451 kg N/day | Sludge for disposal average XND load = 2.9451 kg N/day
Sludge for disposal average SALK load = 1.4632 kmol HCO3/day | Sludge for disposal average SALK load = 1.4632 kmol HCO3/day | Sludge for disposal average SALK load = 1.4632 kmol HCO3/day | Sludge for disposal average SALK load = 1.4632 kmol HCO3/day
Sludge for disposal average TSS load = 2371.615 kg SS/day | Sludge for disposal average TSS load = 2371.615 kg SS/day | Sludge for disposal average TSS load = 2371.615 kg SS/day | Sludge for disposal average TSS load = 2371.615 kg SS/day
Sludge for disposal average SNO2 load = 0.010321 kg N/day | Sludge for disposal average SNO2 load = 0.010321 kg N/day | Sludge for disposal average SNO2 load = 0.010321 kg N/day | Sludge for disposal average SNO2 load = 0.010321 kg N/day
Sludge for disposal average SNO load = 0.00068699 kg N/day | Sludge for disposal average SNO load = 0.00068699 kg N/day | Sludge for disposal average SNO load = 0.00068699 kg N/day | Sludge for disposal average SNO load = 0.00068699 kg N/day
Sludge for disposal average SN2O load = 0.00036463 kg N/day | Sludge for disposal average SN2O load = 0.00036463 kg N/day | Sludge for disposal average SN2O load = 0.00036463 kg N/day | Sludge for disposal average SN2O load = 0.00036463 kg N/day
Sludge for disposal average SN2 load = 5.1531 kg N/day | Sludge for disposal average SN2 load = 5.1531 kg N/day | Sludge for disposal average SN2 load = 5.1531 kg N/day | Sludge for disposal average SN2 load = 5.1531 kg N/day
Sludge for disposal average XBA2 load = 32.8202 kg N/day | Sludge for disposal average XBA2 load = 32.8202 kg N/day | Sludge for disposal average XBA2 load = 32.8202 kg N/day | Sludge for disposal average XBA2 load = 32.8202 kg N/day
Sludge for disposal average Kjeldahl N load = 241.6721 kg N/d | Sludge for disposal average Kjeldahl N load = 241.6721 kg N/d | Sludge for disposal average Kjeldahl N load = 241.672 kg N/d | Sludge for disposal average Kjeldahl N load = 241.672 kg N/d
Sludge for disposal average total N load = 247.4025 kg N/d | Sludge for disposal average total N load = 247.4025 kg N/d | Sludge for disposal average total N load = 247.4025 kg N/d | Sludge for disposal average total N load = 247.4025 kg N/d
Sludge for disposal average total COD load = 3174.162 kg COD/d | Sludge for disposal average total COD load = 3174.162 kg COD/d | Sludge for disposal average total COD load = 3174.162 kg COD/d | Sludge for disposal average total COD load = 3174.162 kg COD/d
Sludge for disposal average BOD5 load = 457.1914 kg BOD5/d | Sludge for disposal average BOD5 load = 457.1914 kg BOD5/d | Sludge for disposal average BOD5 load = 457.1914 kg BOD5/d | Sludge for disposal average BOD5 load = 457.1914 kg BOD5/d
Other effluent quality variables | Other effluent quality variables | Other effluent quality variables | Other effluent quality variables
-------------------------------- | -------------------------------- | -------------------------------- | --------------------------------
Influent Quality Index (IQI) = 52174.9256 kg poll.units/d | Influent Quality Index (IQI) = 52174.9256 kg poll.units/d | Influent Quality Index (IQI) = 52174.9256 kg poll.units/d | Influent Quality Index (IQI) = 52174.9256 kg poll.units/d
Effluent Quality Index (EQI) = 6179.9655 kg poll.units/d | Effluent Quality Index (EQI) = 6179.9655 kg poll.units/d | Effluent Quality Index (EQI) = 6179.9676 kg poll.units/d | Effluent Quality Index (EQI) = 6179.9676 kg poll.units/d
Sludge production for disposal = 16464.2932 kg SS | Sludge production for disposal = 16464.2932 kg SS | Sludge production for disposal = 16464.2931 kg SS | Sludge production for disposal = 16464.2931 kg SS
Average sludge production for disposal per day = 2352.0419 kg SS/d | Average sludge production for disposal per day = 2352.0419 kg SS/d | Average sludge production for disposal per day = 2352.0419 kg SS/d | Average sludge production for disposal per day = 2352.0419 kg SS/d
Sludge production released into effluent = 1625.0192 kg SS | Sludge production released into effluent = 1625.0192 kg SS | Sludge production released into effluent = 1625.0194 kg SS | Sludge production released into effluent = 1625.0194 kg SS
Average sludge production released into effluent per day = 232.1456 kg SS/d | Average sludge production released into effluent per day = 232.1456 kg SS/d | Average sludge production released into effluent per day = 232.1456 kg SS/d | Average sludge production released into effluent per day = 232.1456 kg SS/d
Total sludge production = 18089.3123 kg SS | Total sludge production = 18089.3123 kg SS | Total sludge production = 18089.3125 kg SS | Total sludge production = 18089.3125 kg SS
Total average sludge production per day = 2584.1875 kg SS/d | Total average sludge production per day = 2584.1875 kg SS/d | Total average sludge production per day = 2584.1875 kg SS/d | Total average sludge production per day = 2584.1875 kg SS/d
Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d | Average aeration energy = 4283.3778 kWh/d
Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d | Average pumping energy = 388.17 kWh/d
Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d | Average carbon source addition = 0 kg COD/d
Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d | Average mixing energy = 240 kWh/d
Operational Cost Index | Operational Cost Index | Operational Cost Index | Operational Cost Index
---------------------- | ---------------------- | ---------------------- | ----------------------
Sludge production cost index = 11760.2094 | Sludge production cost index = 11760.2094 | Sludge production cost index = 11760.2094 | Sludge production cost index = 11760.2094
Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778 | Aeration energy cost index = 4283.3778
Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17 | Pumping energy cost index = 388.17
Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0 | Carbon source dosage cost index = 0
Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240 | Mixing energy cost index = 240
Total Operational Cost Index (OCI) = 16671.7572 | Total Operational Cost Index (OCI) = 16671.7572 | Total Operational Cost Index (OCI) = 16671.7571 | Total Operational Cost Index (OCI) = 16671.7571
N2O Emissions | N2O Emissions | N2O Emissions | N2O Emissions
------------------- | ------------------- | ------------------- | -------------------
N2O emission during nitrification/denitrification (ANOX1) = 0.010439 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010439 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010439 kg N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.010439 kg N2O-N/d
N2O emission during nitrification/denitrification (ANOX2) = 0.011131 kg N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.011131 kg N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.011131 kg N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.011131 kg N2O-N/d
N2O emission during nitrification/denitrification (AER1) = 1.2185 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.2185 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.2185 kg N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.2185 kg N2O-N/d
N2O emission during nitrification/denitrification (AER2) = 0.60809 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.60809 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.60809 kg N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.60809 kg N2O-N/d
N2O emission during nitrification/denitrification (AER3) = 0.27686 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.27686 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.27686 kg N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.27686 kg N2O-N/d
N2O emission during nitrification/denitrification (total) = 2.125 kg N2O/d | N2O emission during nitrification/denitrification (total) = 2.125 kg N2O/d | N2O emission during nitrification/denitrification (total) = 2.125 kg N2O/d | N2O emission during nitrification/denitrification (total) = 2.125 kg N2O-N/d
N2O emission during nitrification/denitrification (ANOX1) = 0.016405 kg N-N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.016405 kg N-N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.016405 kg N-N2O/d | N2O emission during nitrification/denitrification (ANOX1) = 0.016405 kg N2O/d
N2O emission during nitrification/denitrification (ANOX2) = 0.017492 kg N-N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.017492 kg N-N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.017492 kg N-N2O/d | N2O emission during nitrification/denitrification (ANOX2) = 0.017492 kg N2O/d
N2O emission during nitrification/denitrification (AER1) = 1.9147 kg N-N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.9147 kg N-N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.9147 kg N-N2O/d | N2O emission during nitrification/denitrification (AER1) = 1.9147 kg N2O/d
N2O emission during nitrification/denitrification (AER2) = 0.95557 kg N-N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.95557 kg N-N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.95557 kg N-N2O/d | N2O emission during nitrification/denitrification (AER2) = 0.95557 kg N2O/d
N2O emission during nitrification/denitrification (AER3) = 0.43506 kg N-N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.43506 kg N-N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.43506 kg N-N2O/d | N2O emission during nitrification/denitrification (AER3) = 0.43506 kg N2O/d
N2O emission during nitrification/denitrification (total) = 3.3393 kg N-N2O/d | N2O emission during nitrification/denitrification (total) = 3.3393 kg N-N2O/d | N2O emission during nitrification/denitrification (total) = 3.3393 kg N-N2O/d | N2O emission during nitrification/denitrification (total) = 3.3393 kg N2O/d
Effluent violations | Effluent violations | Effluent violations | Effluent violations
------------------- | ------------------- | ------------------- | -------------------
95% percentile for effluent SNH (Ammonia95) = 6.8302 g N/m3 | 95% percentile for effluent SNH (Ammonia95) = 6.8302 g N/m3 | 95% percentile for effluent SNH (Ammonia95) = 6.8302 g N/m3 | 95% percentile for effluent SNH (Ammonia95) = 6.8302 g N/m3
95% percentile for effluent TN (TN95) = 22.7697 g N/m3 | 95% percentile for effluent TN (TN95) = 22.7697 g N/m3 | 95% percentile for effluent TN (TN95) = 22.7697 g N/m3 | 95% percentile for effluent TN (TN95) = 22.7697 g N/m3
95% percentile for effluent TSS (TSS95) = 15.5764 g SS/m3 | 95% percentile for effluent TSS (TSS95) = 15.5764 g SS/m3 | 95% percentile for effluent TSS (TSS95) = 15.5764 g SS/m3 | 95% percentile for effluent TSS (TSS95) = 15.5764 g SS/m3
The maximum effluent total nitrogen level (18 mg N/l) was violated | The maximum effluent total nitrogen level (18 mg N/l) was violated | The maximum effluent total nitrogen level (18 mg N/l) was violated | The maximum effluent total nitrogen level (18 mg N/l) was violated
during 3.0625 days, i.e. 43.75% of the operating time. | during 3.0625 days, i.e. 43.75% of the operating time. | during 3.0625 days, i.e. 43.75% of the operating time. | during 3.0625 days, i.e. 43.75% of the operating time.
The limit was violated at 7 different occasions. | The limit was violated at 7 different occasions. | The limit was violated at 7 different occasions. | The limit was violated at 7 different occasions.
The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated | The maximum effluent ammonia nitrogen level (4 g N/m3) was violated
during 0.83333 days, i.e. 11.9048% of the operating time. | during 0.83333 days, i.e. 11.9048% of the operating time. | during 0.83333 days, i.e. 11.9048% of the operating time. | during 0.83333 days, i.e. 11.9048% of the operating time.
The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions. | The limit was violated at 5 different occasions.
***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished ***** | ***** Plant evaluation of BSM2 system successfully finished *****
End time (hour:min:sec) = 13 33 19 | End time (hour:min:sec) = 14 6 50 | End time (hour:min:sec) = 9 23 52 | End time (hour:min:sec) = 9 17 36